## April-19
VEH - Vizianagaram, 7.29 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [5 empty] | Power Generation | [17 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [5 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative APRIL-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Total irradiation(KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | (kWh/kWp) |  |  | W/m2 | (km/h) | (°C) | (°C) | (%) |  | (%)
2019-04-01 | 6:01 | 17:53 | 11:52 | 4684 | 5381 | 5443 | 4557 | 4165 | 5566 | 29796 | 29700 | 96 | 0.3232% | 200 | 296 | 29796 | 29796 | 4.0872 | 5.9327 | 5932.68 | 500.03 | 0.27 | 33.01 | 38.64 | 68.88% | 5.9 | 17.03% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 . | 12:44:00,15:23:00 & 06:01:00 | 12:53:00 , 16:19:00 &17:53:00 | 01:05:00 &11:52:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 1 To 10 (31 tables) Module cleaning work completed. 5.ICR-1 INV-1 SMB 1 to 4 all string Current and Voc checking work completed.
2019-04-02 | 6:15 | 17:58 | 11:43 | 5319 | 5787 | 5829 | 4887 | 6129 | 5997 | 33948 | 33700 | 248 | 0.7359% | 100 | 348 | 63744 | 63744 | 4.6568 | 6.5817 | 6581.72 | 556.01 | 0.08 | 33.35 | 38.26 | 70.58% | 6.57 | 19.4% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 . | 07:40 & 6:15 | 07:50 & 17:58 | 00:10:00 & 11:43:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 11 To 20 (46 tables) Module cleaning work completed. 4. Block no 18 to 19 (10 tables) grass cutting completed. 5.ICR-1 INV-1 SMB 5 to 7 all string Current and Voc checking work completed.
2019-04-03 | 6:02 | 17:57 | 11:55 | 3666 | 3988 | 3957 | 3363 | 3765 | 4140 | 22879 | 22700 | 179 | 0.7885% | 100 | 279 | 86623 | 86623 | 3.1384 | 5.118 | 5118 | 422.48 | 0.03 | 31.94 | 35.83 | 63.4% | 5.1 | 13.08% | 11:42 | 11:08 | Grid failure at 132 KV GSS | 0:34 | icr-2 in inv-1 Node1. | 6:02 | 17:57 | 11:55 | Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 15 To 25 (45 tables) Module cleaning work completed. 4. Block no 17 (26 tables) grass cutting completed. 5.ICR-1 INV-2 SMB 1 to 4 all string Current and Voc checking work completed.
2019-04-04 | 6:02 | 17:47 | 11:45 | 4716 | 5206 | 5128 | 4317 | 4575 | 5292 | 29234 | 29000 | 234 | 0.8069% | 200 | 434 | 115857 | 115857 | 4.0102 | 5.567 | 5567 | 473.32 | 0.01 | 32.22 | 36.9 | 71.1% | 5.56 | 16.71% |  |  |  | 0:00 | icr-2 in inv-1 Node1. | 6:02 | 17:47 | 11:45 | Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 24 To 32 (49 tables) Module cleaning work completed. 4. Block no 25 (11 tables) grass cutting completed. 5.ICR-1 INV-2 SMB 5 to 7 all string Current and Voc checking work completed.
2019-04-05 | 6:00 | 17:57 | 11:57 | 4992 | 5550 | 5487 | 4583 | 4992 | 5620 | 31224 | 31100 | 124 | 0.3987% | 200 | 324 | 147081 | 147081 | 4.2831 | 6.1335 | 6133.48 | 497.12 | 0.06 | 32.96 | 39.22 | 73.33% | 6.1 | 17.85% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 . | 13:09:00, 13:33:00 &06:00:00 | 13:19:00, 14:03:00 & 17:57:00 | 00:40:00 & 11:57:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 18,21,25&33 (50 tables) Module cleaning work completed. 4. ICR-1 INV-3 SMB 1 to 4 all string Current and Voc checking work completed with damage modules checking (Not Found).
2019-04-06 | 6:04 | 16:37 | 10:33 | 3586 | 3975 | 4022 | 3273 | 3818 | 4086 | 22760 | 22500 | 260 | 1.156% | 200 | 460 | 169841 | 169841 | 3.1221 | 4.3186 | 4318.65 | 408.82 | 0.035 | 32.72 | 38.06 | 63.91% | 4.3 | 13.01% |  |  |  | 0:00 | icr-2 in inv-1 Node1. | 6:04 | 16:37 | 10:33 | Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 38&42 (35 tables) Module cleaning work completed. 4. ICR-1 INV-3 SMB 5 to 7 all string Current and Voc checking work completed with damage modules checking (Not Found).
2019-04-07 | 5:58 | 18:00 | 12:02 | 5184 | 5708 | 5719 | 4807 | 5395 | 5913 | 32726 | 32500 | 226 | 0.6954% | 200 | 426 | 202567 | 202567 | 4.4892 | 6.7815 | 6781.54 | 563.51 | 0.0966 | 31.79 | 38.56 | 75.51% | 6.81 | 18.7% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 . | 07:29, 14:46, &05:58:00 | 07:34, 15:01 &18:00 | 00:20:00 & 12:02:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.Block no 43 to 48 (36 tables) Module cleaning work completed. 4. ICR-2 INV-1 SMB 1 to 4 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-08 | 5:58 | 17:56 | 11:58 | 5128 | 5632 | 5743 | 4734 | 4848 | 5839 | 31924 | 31600 | 324 | 1.025% | 100 | 424 | 234491 | 234491 | 4.3791 | 6.2656 | 6265.61 | 525.07 | 0.06 | 32 | 36.58 | 69.31% | 6.3 | 18.25% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 . | 08:10, 08:53, 11:27&05:58 | 08:18, 09:06, 11:39&17:56 | 00:33:00&11:58 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 49,50,51 (10) modules cleaning work completed 4.Block no 24 to 25 (12 tables) Grass cutting work completed. 5. ICR-2 INV-1 SMB 5 to 7 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-09 | 5:57 | 17:56 | 11:59 | 4382 | 4803 | 4925 | 4084 | 4774 | 5032 | 28000 | 27800 | 200 | 0.7194% | 200 | 400 | 262491 | 262491 | 3.8409 | 5.2354 | 5235.41 | 436.14 | 0.01 | 32 | 36.19 | 73.59% | 5.23 | 16% |  |  |  | 0:00 | icr_2 inv-1 & inv-1 | 13:03&05:57 | 13:15&13:15 | 00:12:00&11:59 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 50 to 57 (50) modules cleaning work completed 4. ICR-2 INV-2 SMB 1 to 4 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-10 | 5:57 | 17:54 | 11:57 | 5090 | 5605 | 5384 | 4834 | 5982 | 5857 | 32752 | 32500 | 252 | 0.7754% | 200 | 452 | 295243 | 295243 | 4.4927 | 6.2525 | 6252.53 | 522.69 | 0.09 | 33 | 39.02 | 71.73% | 6.25 | 18.72% |  |  |  | 0:00 | icr-1 inv-3 & Icr-2 inv-1 | 08:50&05:57 | 09:00 & 17:54 | 00:10:00 & 11:57 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 52 to 61 (50) modules cleaning work completed 4. ICR-2 INV-2 SMB 5 to 7 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-11 | 5:55 | 17:54 | 11:59 | 4501 | 4959 | 5079 | 4072 | 5123 | 5251 | 28985 | 28700 | 285 | 0.993% | 100 | 385 | 324228 | 324228 | 3.976 | 5.5894 | 5589.37 | 465.7 | 0.02 | 34 | 39.55 | 71.44% | 5.58 | 16.57% |  |  |  | 0:00 | icr-2 inv-1 & Icr-2 inv-2 | 07:25, 05:55 & 09:00 | 08:06, 17:54 & 09:10 | 00;41:00, 11:54 & 00:10:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 63 to 66 (20 Tables) modules cleaning work completed 4. ICR-2 INV-3 SMB 1 to 4 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-12 | 5:54 | 17:38 | 11:44 | 4767 | 5249 | 5386 | 4580 | 4786 | 5517 | 30285 | 30000 | 285 | 0.95% | 200 | 485 | 354513 | 354513 | 4.1543 | 5.9514 | 5951.45 | 507.42 | 0.1 | 35 | 40.99 | 68.32% | 5.96 | 17.31% |  |  |  | 0:00 | icr-2 inv-1 & Icr-2 inv-2 | 05:54 & 11:04, 11:17 | 17:44 & 11:09, 11:27 | 11:44 & 00:15:00 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 52 to 81 (45 Tables) modules cleaning work completed 4. ICR-2 INV-3 SMB 5 to 7 all string Current checking work completed with damage modules checking (Not Found). Voc and cable dressing not checked due to less manpower.
2019-04-13 | 5:50 | 17:50 | 12:00 | 4930 | 5434 | 5557 | 4696 | 5407 | 5649 | 31673 | 31500 | 173 | 0.5492% | 200 | 373 | 386186 | 386186 | 4.3447 | 6.148 | 6148 | 511.59 | 0 | 35 | 41.5 | 72.38% | 6.15 | 18.1% |  |  |  | 0:00 | Icr-2 inv-2 | 10:47 | 10:35 | -0.0083333 | contactor problem | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 81 (33 Tables) modules cleaning work completed. 4.Earth pit checking.
2019-04-14 | 5:51 | 17:52 | 12:01 | 4904 | 5408 | 5530 | 4716 | 5965 | 5713 | 32236 | 32000 | 236 | 0.7375% | 100 | 336 | 418422 | 418422 | 4.4219 | 6.343 | 6343 | 529.84 | 0.09 | 34 | 41.85 | 69.55% | 6.34 | 18.42% |  |  |  | 0:00 | icr-2 inv-1 | 5:51 | 17:52 | 12:01 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 71 (35 Tables) modules cleaning work completed.
2019-04-15 | 5:51 | 17:49 | 11:58 | 5039 | 5551 | 5662 | 4462 | 6449 | 5917 | 33080 | 32800 | 280 | 0.8537% | 200 | 480 | 451502 | 451502 | 4.5377 | 6.33 | 6330 | 528.98 | 0.12 | 35 | 41.68 | 71.39% | 6.33 | 18.91% |  |  |  | 0:00 | icr-2 inv-1 | 5:51 | 17:49 | 11:58 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 78 TO 80 (30 Tables) modules cleaning work completed.
2019-04-16 | 5:52 | 17:50 | 11:58 | 5242 | 5763 | 5891 | 4991 | 5686 | 6252 | 33825 | 33200 | 625 | 1.883% | 100 | 725 | 485327 | 485327 | 4.6399 | 5.097 | 5097 | 629.85 | 0.08 | 35 | 41.65 | 61.56% | 5.06 | 19.33% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 | 05:51:00 13:20 | 17:50:00 13:05 | #VALUE! | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 70 TO 77 (55 Tables) modules cleaning work completed. 4. MCR, ICR-1&2 Battery and Ups maintenance
2019-04-17 | 5:50 | 17:58 | 12:08 | 5571 | 6170 | 6271 | 5051 | 6090 | 6748 | 35901 | 35600 | 301 | 0.8455% | 200 | 501 | 521228 | 521228 | 4.9247 | 7.169 | 7169 | 590.04 | 0.16 | 34 | 40.52 | 69.75% | 7.16 | 20.52% |  |  |  | 0:00 | icr-2 inv-2 & inv-1 | 05:50:00 & 10:51, 14:03 | 17:58 & 10:45, 13:40 | #VALUE! | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . & HW desk | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 32 TO 27 (35 Tables) modules cleaning work completed. 4. Lt pannel Cleaning in MCR & ICR's
2019-04-18 | 5:50 | 18:00 | 12:10 | 5126 | 5821 | 5754 | 4760 | 6246 | 6169 | 33876 | 33600 | 276 | 0.8214% | 100 | 376 | 555104 | 555104 | 4.6469 | 6.43 | 6430 | 528.06 | 0.19 | 33 | 39 | 72.53% | 6.43 | 19.36% |  |  |  | 0:00 | icr-2 in inv-1 Node1. | 5:50 | 18:00 | 12:10 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 27 TO 15 (47 Tables) modules cleaning work completed. 4.RTU & MTU pannel Cleaning.
2019-04-19 | 5:49 | 17:07 | 11:18 | 4069 | 5058 | 5007 | 4247 | 5473 | 5403 | 29257 | 29000 | 257 | 0.8862% | 200 | 457 | 584361 | 584361 | 4.0133 | 5.557 | 5557 | 490.16 | 0.13 | 33 | 39.43 | 67.3% | 5.56 | 16.72% |  |  |  | 0:00 | icr-2 in inv-1 Node1. | 5:49 | 17:06 | 11:17 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no 11 TO 17 ( 33 Tables) modules cleaning work completed. 4. Weather station maintenance.
2019-04-20 | 5:55 | 17:15 | 11:20 | 4470 | 4941 | 4966 | 4111 | 5305 | 5202 | 28995 | 28800 | 195 | 0.6771% | 200 | 395 | 613356 | 613356 | 3.9774 | 5.739 | 5739 | 505.55 | 0.16 | 31 | 37.57 | 69.62% | 5.74 | 16.57% |  |  |  | 0:00 | icr-2 in inv-1 Node1. | 5:55 | 17:15 | 11:20 | HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3.bl0ck no ( Tables) modules cleaning work completed. 4. fire extingshire maintenance.
2019-04-21 | 5:50 | 17:34 | 11:44 | 4247 | 3045 | 4684 | 4171 | 5341 | 5238 | 26726 | 26500 | 226 | 0.8528% | 100 | 326 | 640082 | 640082 | 3.6661 | 5.407 | 5407 | 460.15 | 0.2 | 30 | 35.84 | 70.3% | 5.41 | 15.28% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:50 | 17:35 | 11:45 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned today again 4. Due to Inverter Problem and rain today Shedule was not Completed.
2019-04-22 | 5:54 | 17:55 | 12:01 | 5486 | 5046 | 5949 | 5261 | 6627 | 6436 | 34805 | 34600 | 205 | 0.5925% | 200 | 405 | 674887 | 674887 | 4.7743 | 6.773 | 6773 | 562.52 | 0.03 | 33 | 40.44 | 72.34% | 6.77 | 19.89% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:54 | 17:55 | 12:01 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Transformer and Street light maintenance.
2019-04-23 | 5:46 | 18:15 | 12:29 | 5304 | 4962 | 5762 | 5042 | 6378 | 6256 | 33704 | 33500 | 204 | 0.609% | 100 | 304 | 708591 | 708591 | 4.6233 | 6.588 | 6588 | 524.8 | 0.33 | 32 | 38.41 | 73.31% | 6.59 | 19.26% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:46 | 18:15 | 12:29 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Transformer and Street light maintenance.
2019-04-24 | 5:45 | 18:00 | 12:15 | 5500 | 4961 | 5973 | 5058 | 6591 | 6444 | 34527 | 34200 | 327 | 0.9561% | 200 | 527 | 743118 | 743118 | 4.7362 | 6.763 | 6763 | 551.23 | 0.07 | 33 | 40.62 | 68.83% | 6.76 | 19.73% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:45 | 18:00 | 12:15 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4.Street light maintenance.
2019-04-25 | 5:46 | 18:02 | 12:16 | 5209 | 4859 | 5643 | 4835 | 6241 | 6092 | 32879 | 32700 | 179 | 0.5234% | 200 | 379 | 775997 | 775997 | 4.5102 | 6.38 | 6380 | 519.03 | 0.08 | 33.39 | 39.89 | 70.94% | 6.3 | 18.79% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:46 | 18:02 | 12:16 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Visual inspection and check points of checklist HT Switching Yard
2019-04-26 | 5:44 | 17:38 | 11:54 | 4980 | 4657 | 5419 | 4168 | 5969 | 5810 | 31003 | 31000 | 3 | 0.009174% | 200 | 203 | 807000 | 807000 | 4.2528 | 6.1591 | 6159.1 | 516.72 | 0.018 | 33.9958 | 40.88 | 67.1% | 6.15 | 17.72% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:44 | 17:38 | 11:54 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Visual inspection and check points of checklist HT Switching Yard 5. All Tickets cannot finished, Due to less manpower.
2019-04-27 | 5:40 | 18:06 | 12:26 | 4899 | 4570 | 5307 | 4517 | 5881 | 5733 | 30907 | 30700 | 207 | 0.6677% | 200 | 407 | 837907 | 837907 | 4.2396 | 6.0546 | 6054.6 | 486.31 | 0.048 | 34.46 | 40.41 | 73.26% | 6.05 | 17.67% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:40 | 18:06 | 12:26 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Visual inspection and check all Street lights, ICR 2 all light's and new 3Mwp all light's power supply is off. because all connection given from new plant. 5. All Tickets cannot finished, Due to less manpower.
2019-04-28 | 5:46 | 17:55 | 12:09 | 4923 | 4578 | 5313 | 4437 | 5860 | 5712 | 30823 | 30600 | 223 | 0.7264% | 100 | 323 | 868730 | 868730 | 4.2281 | 6.0611 | 6061.11 | 497.2 | 0.026 | 34.24 | 40.27 | 68.4% | 6.06 | 17.62% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:46 | 17:55 | 12:09 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Visual inspection and check RO plant & Routine Physical Inspection of Lightening Arrestor 5. All Tickets cannot finished, Due to less manpower.
2019-04-29 | 5:41 | 17:51 | 12:10 | 5260 | 4909 | 5699 | 4940 | 6273 | 6143 | 33224 | 32900 | 324 | 1.059% | 200 | 524 | 901954 | 901954 | 4.5575 | 6.5949 | 6594.92 | 541.36 | 0.0758 | 34.595 | 41.52 | 69.29% | 6.59 | 18.99% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:41 | 17:51 | 12:10 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Inverter cleaning & Check the Emergency stop working condition. 5. All Tickets cannot finished, Due to less manpower.
2019-04-30 | 5:45 | 18:04 | 12:19 | 5160 | 4834 | 5598 | 4733 | 6189 | 6010 | 32524 | 32300 | 224 | 0.732% | 200 | 424 | 934478 | 934478 | 4.4615 | 6.4744 | 6474.42 | 525.94 | 0.06 | 33.95 | 41.08 | 69.72% | 6.47 | 18.59% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:45 | 18:04 | 12:19 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Due to rain Modules are cleaned. 4. Inverter cleaning not completed due to less time, 3 modules had damaged due to yesterday night high speed storm. now we were replaced that 3nos module. 5. All Tickets cannot finished, Due to less manpower.
|  |  |  | 146334 | 152410 | 162087 | 136287 | 166323 | 171037 | 934478 | 927300 |  |  | 5000 | 12178

## May-19
VEH - Vizianagaram, 7.29 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [5 empty] | Power Generation | [19 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [5 empty] | Day's Generation (all inverters) | S/Y Reading (MWh) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative MAY-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Total irradiation(KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | kWh | MWh | kWh | kWh | % | kWh | kWh | kWh | kWh | (kWh/kWp) |  |  | W/m2 | (km/h) | (°C) | (°C) | (%) | (%) |  | (%)
2019-05-01 | 5:40 | 17:40 | 12:00 | 3955 | 3705 | 4245 | 3426 | 4557 | 4553 | 24441 | 17552.8 | 24300 | 141 | 0.5802% | 100 | 241 | 24441 | 958919 | 3.3527 | 4.6106 | 4610.6 | 386.97 | 1.154 | 32.31 | 36.01 | 72.2% | 69.15% | 4.6436 | 13.97% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:40 | 17:40 | 12:00 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning at frist half 25nos table, secnd half at modules tighten at ICR-1. 4. ICR-1 INV-1 SMB 1 to 4 all string Current and Voc checking work completed.
2019-05-02 | 5:52 | 17:46 | 11:54 | 1694 | 1614 | 1817 | 1037 | 1635 | 1959 | 9756 | 17562.3 | 9500 | 256 | 2.695% | 200 | 456 | 34197 | 968675 | 1.3383 | 1.602 | 1602.01 | 134.55 | 0.0898 | 29.45 | 28.15 | 83.58% | 82.57% | 1.6146 | 5.576% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 5:52 | 17:46 | 11:54 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-1 INV-1 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV1, Node 1&2 two conductor had been interchange, From tomorrow Node 2 is not working Due to PI saturation, one conductor need to replace.
2019-05-03 | 6:18 | 18:01 | 11:43 | 2304 | 2187 | 2469 | 1121 | 1966 | 2586 | 12633 | 17574.8 | 12500 | 133 | 1.064% | 200 | 333 | 46830 | 981308 | 1.7329 | 2.4714 | 2471.42 | 211.45 | 0.1427 | 31.048 | 32.088 | 69.95% | 68.04% | 2.5374 | 7.221% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown | 6:18 | 18:01 | 11:43 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-1 INV-2 SMB 1 to 4 all string, SMB, Modules Visulally checking work completed. 5. ICR1, INV2,INV1 structure tighten checked.
2019-05-04 | 5:45 | 18:01 | 12:16 | 4671 | 4413 | 4964 | 4406 | 3771 | 5331 | 27556 | 17602.1 | 27300 | 256 | 0.9377% | 200 | 456 | 74386 | 1008864 | 3.78 | 5.6714 | 5671.38 | 462.03 | 0.035 | 32.79 | 39.26 | 66.69% | 63.04% | 5.5444 | 15.75% |  |  |  | 0:00 | 1.icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV2.2 | 05:45:00 09:55:00&14:20:00 | 18:01:00 10:10&14:46 | 12:16:00 & 00:41:00 | 1.HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-1 INV-2 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR1, INV3 structure tighten checked. 6. All SMB Com-Card Visulally Checked by team.
2019-05-05 | 5:49 | 17:58 | 12:09 | 4405 | 4170 | 0 | 5164 | 5042 | 5507 | 24288 | 17626.2 | 24100 | 188 | 0.7801% | 100 | 288 | 98674 | 1033152 | 3.3317 | 5.98 | 5980 | 491.22 | 0.02 | 33.84 | 41.69 | 55.82% | 52.25% | 5.8946 | 13.88% | 7:22 | 6:55 | Grid Off due to Inv fault | 0:27 | 1. icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-1 INV-3 Shutdown. | 5:49 | 17:58 | 12:09 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. AC Braker Issue. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-1 INV-3 SMB 1 to 4 all string, SMB, Modules Visulally checking work completed. 5. ICR1, INV3 structure tighten checked. 6. All SMB Com-Card Visulally Checked by team. 7. Inv 1.3 AC site breaker has burn, so now inverter is in off condition.
2019-05-06 | 5:40 | 18:08 | 12:28 | 4134 | 3898 | 0 | 4585 | 3878 | 4855 | 21350 | 17647.4 | 21200 | 150 | 0.7075% | 200 | 350 | 120024 | 1054502 | 2.9287 | 5.3395 | 5339.52 | 428.3 | 0.345 | 32.74 | 39.43 | 54.85% | 51.81% | 5.1396 | 12.2% | 13:06:00 & 17:07:00 | 13:02:00 & 15:25:00 | 1. Grid Off from substation. 2. Grid Trip due to Rain. | 00:04:00 & 01:42:00 | 1. icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-1 INV-3 Shutdown. 4. ICR-2 INV-2 | 05:40:00, 10:30:00 &12:30:00 | 18:08:00, 10:38:00 & 12:44:00 | 1. 12:28:00 2. 12:28:00 3. 12:28:00 4. 00:22:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. AC Braker Issue. 4. RTM rellay Problem - contactor 121. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain (today). 4. ICR-1 INV-3 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR1, INV3 structure tighten checked. 6. Due to Rain and air stream two nos trees falling on 33KV over head line, within 2hr its removed and start plant. 7. Inv 1.3 AC site breaker has burn, so now inverter is in off condition.
2019-05-07 | 5:37 | 18:02 | 12:25 | 3257 | 1557 | 705 | 5094 | 3179 | 5360 | 19152 | 17666.3 | 18900 | 252 | 1.333% | 200 | 452 | 139176 | 1073654 | 2.6272 | 5.5874 | 5587.42 | 445.36 | 0.31 | 33.23 | 39.1 | 47.51% | 44.94% | 5.3443 | 10.95% |  |  |  | 0:00 | 1. icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-1 INV-3 Shutdown. 4. ICR-2 INV-2 5. ICR-1 INV-1 SMB-5 6. ICR-1 INV-2 SMB-6&3 | 1. 05:37:00, 2. 05:37:00 3. 05:37:00 4. 12:10:00 & 14:40:00 5. 05:37:00 6. 05:37:00 | 1. 18:02:00, 2. 18:02:00, 3.14:11:00 4. 13:20:00 & 15:10:00 5. 18:02:00 6. 18:02:00 | 1. 12:25:00 2. 12:25:00 3. 08:34:00 4. 01:40:00 5. 12:25:00 6. 12:25:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. AC Braker Issue. 4. RTM rellay Problem - contactor 121. 5&6. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain (today). 4. ICR-2 INV-1 SMB 1 to 4 all string, SMB, Modules Visulally checking work not completed due to emergency work at ICR-1 all SMB's. 5. ICR2, INV1 structure tighten checked INV1.1 Cables dressing. 6. Due to Rain ICR-1, INV-1, SMB-5 and ICR-1, INV-2, SMB-6&3 was in manual off condition due to ground fault. 7. Inv 1.3 AC site breaker has burn, so now inverter is in off condition. today at 14:11:00 it was start with help of engiteam engineer.
2019-05-08 | 5:38 | 17:39 | 12:01 | 3914 | 2950 | 4997 | 5149 | 5317 | 5472 | 27799 | 17694 | 27700 | 99 | 0.3574% | 200 | 299 | 166975 | 1101453 | 3.8133 | 5.7315 | 5731.53 | 476.23 | 0.0069 | 34.65 | 39.49 | 66.63% | 62.93% | 5.7148 | 15.89% |  |  |  | 0:00 | 1. icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV-2 4. ICR-1 INV-1 SMB-5 5. ICR-1 INV-2 SMB-6&3 | 1. 05:38:00, 2. 05:38:00 3. 08:03:00 4. 05:37:00 5. 05:37:00 | 1. 17:39:00, 2. 17:39:00, 3. 08:14:00 4. 17:39:00 5. 17:39:00 | 1. 12:01:00 2. 12:01:00 3. 00:11:00 4. 12:01:00 5. 12:01:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. 4&5. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-2 INV-1 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV3 structure tighten checked. 6. Due to Rain ICR-1, INV-1, SMB-5 and ICR-1, INV-2, SMB-6&3 was in manual off condition due to ground fault. SMB-6 problem solved, string no 14 MC4 connectors had problems. 7. ICR-2 one AC is not working.
2019-05-09 | 5:35 | 18:16 | 12:41 | 3720 | 3131 | 4820 | 4889 | 4380 | 5225 | 26165 | 17719.8 | 25800 | 365 | 1.415% | 200 | 565 | 193140 | 1127618 | 3.5892 | 5.4953 | 5495.34 | 432.67 | 0.01 | 34.93 | 39.79 | 65.4% | 61.69% | 5.192 | 14.95% |  |  |  | 0:00 | 1. icr-2 in inv-1 Node1. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV-2 4. ICR-1 INV-1 SMB-5 5. ICR-1 INV-2 SMB-3 | 1. 05:35:00, 2. 05:35:00 3. 08:03:00 4. 05:35:00 5. 05:35:00 | 1. 18:16:00, 2. 18:16:00, 3. 08:11:00 4. 18:16:00 5. 18:16:00 | 1. 12:41:00 2. 12:41:00 3. 00:08:00 4. 12:41:00 5. 12:41:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. 4&5. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-2 INV-2 SMB 1 to 4 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV2 structure tighten checked. 6. Due to Rain ICR-1, INV-1, SMB-5 and ICR-1, INV-2, SMB-3 was in manual off condition due to ground fault. SMB-3 problem not solved but we are found faulty string is string no 14, need to change nagative side cable. 7. ICR-2 one AC is not working.
2019-05-10 | 5:38 | 17:48 | 12:10 | 4097 | 3719 | 4739 | 5081 | 4359 | 5381 | 27376 | 17747 | 27200 | 176 | 0.6471% | 200 | 376 | 220516 | 1154994 | 3.7553 | 5.7134 | 5713.41 | 468.56 | 0.01 | 34.9 | 39.61 | 65.87% | 62.18% | 5.6227 | 15.65% |  |  |  | 0:00 | 1. icr-2 in inv-1 Node2. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV-2 4. ICR-1 INV-1 SMB-5 5. ICR-1 INV-2 SMB-3 | 1. 05:38:00, 2. 05:38:00 3. 13:20:00 4. 05:38:00 5. 05:38:00 | 1. 17:48:00, 2. 17:48:00, 3. 13:30:00 4. 13:15:00 5. 17:48:00 | 1. 12:10:00 2. 12:10:00 3. 00:10:00 4. 07:37:00 5. 12:10:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. 4&5. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-2 INV-2 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV2 structure tighten checked. 6. Due to Rain ICR-1, INV-1, SMB-5 and ICR-1, INV-2, SMB-3 was in manual off condition due to ground fault. SMB-3 problem not solved but we are found faulty string is string no 14, need to change nagative side cable. today SMB5 string 9 found problem,now SMB 5 is running with out string 9. 7. ICR-2 one AC is not working.
2019-05-11 | 5:37 | 17:52 | 12:15 | 4200 | 3375 | 4501 | 4472 | 4723 | 4859 | 26130 | 17773 | 26000 | 130 | 0.5% | 200 | 330 | 246646 | 1181124 | 3.5844 | 5.1368 | 5136.83 | 420.1 | 0.04 | 34.29 | 37.73 | 69.65% | 66.25% | 5.0412 | 14.93% | 15:40 | 15:35 | Grid Off due to over voltage | 0:05 | 1. icr-2 in inv-1 Node2. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV-2 4. ICR-1 INV-2 SMB-3 | 1. 05:37:00, 2. 05:37:00 3. 15:20:00 4. 05:37:00 | 1. 17:52:00, 2. 17:52:00, 3. 15:35:00 4. 17:52:00 | 1. 12:15:00 2. 12:15:00 3. 00:15:00 4. 12:15:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. 4. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-2 INV-3 SMB 1 to 4 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV2&3 structure tighten checked. 6. Due to rain till SMB-3 insulation fault not clear, other two SMB is working. 7. ICR-2 one AC is not working.
2019-05-12 | 5:43 | 18:06 | 12:23 | 3990 | 3215 | 4219 | 4382 | 4661 | 4713 | 25180 | 17798 | 25000 | 180 | 0.72% | 200 | 380 | 271826 | 1206304 | 3.454 | 4.9853 | 4985.32 | 402.2 | 0.16 | 32.44 | 36.74 | 69.35% | 66.22% | 4.8264 | 14.39% |  |  |  | 0:00 | 1. icr-2 in inv-1 Node2. 2. icr.1,inv-2 smb-5 shutdown, 3. ICR-2 INV-2 4. ICR-1 INV-2 SMB-3 | 1. 05:43:00, 2. 05:43:00 3. 06:37:00 4. 05:43:00 | 1. 18:06:00, 2. 18:06:00, 3. 06:42:00 4. 18:06:00 | 1. 12:23:00 2. 12:23:00 3. 00:05:00 4. 12:23:00 | 1. HW and contactor-121 fault & Current PI saturation, Inverter runned on 3 nodes . 2. Due to Communication Card failure. 3. RTM rellay Problem - contactor 121. 4. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. ICR-2 INV-3 SMB 5 to 7 all string, SMB, Modules Visulally checking work completed. 5. ICR2, INV2&1 structure tighten checked. 6. Substation grass cutting completed today. 7. Due to rain till SMB-3 insulation fault not clear, other two SMB is working. 8. ICR-2 one AC is not working.
2019-05-13 | 5:37 | 17:47 | 12:10 | 3632 | 2914 | 3796 | 4011 | 4387 | 4255 | 22995 | 17820.8 | 22800 | 195 | 0.8553% | 200 | 395 | 294821 | 1229299 | 3.1543 | 4.3007 | 4300.7 | 352.22 | 0.014 | 32.41 | 36.31 | 73.61% | 70.41% | 4.2266 | 13.14% |  |  |  | 0:00 | 1. icr.1,inv-2 smb-5 shutdown, 2. ICR-1 INV-2 SMB-3 | 1. 05:37:00, 2. 05:37:00 | 1. 17:47:00, 2. 17:47:00 | 1. 12:10:00 2. 12:10:00 | 1. Due to Communication Card failure. 2. Ground fault due to rain. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is completed due to rain. 4. All Earth pit Visulally checking work completed. 5. ICR2, INV1 structure tighten checked. 6. ICR 2, Inv-1&2 Problem has been solved from today. 7. Due to rain till SMB-3 insulation fault not clear, other two SMB is working. 8. ICR-2 one AC is not working.
2019-05-14 | 5:31 | 18:07 | 12:36 | 4949 | 2995 | 5193 | 5524 | 5969 | 5790 | 30420 | 17851.1 | 30300 | 120 | 0.396% | 100 | 220 | 325241 | 1259719 | 4.1728 | 6.1763 | 6176.31 | 489.75 | 0.05 | 34.91 | 39.8 | 67.62% | 63.78% | 5.877 | 17.39% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-7 2. ICR-1, INV-2, SMB-5 3. ICR-1, INV-2, SMB-3 | 1. 07:45:00, 2. 05:31:00 3. 07:45:00 | 1. 13:55:00, 2. 18:07:00, 3. 13:17:00. | 1. 06:10:00 2. 12:36:00 3. 05:32:00 | 1. Ground fault due to rain. Found faulty at 1nos of strings(13). 2. Due to Communication Card failure. 3. Ground fault due to rain. Found faulty at 3nos of strings(10,12&13) | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. Module Cleaning is start at today, today completed 20 nos of table at INV-1.2. 4. ICR-1 All inverters cleaning work completed. 5. 3nos SMB of INV-1.2 was down at morning due to ground fault, now found the faulty strings and start SMBs. 6. ICR-2 one AC is not working.
2019-05-15 | 5:35 | 17:45 | 12:10 | 4334 | 3910 | 4710 | 4533 | 4992 | 5076 | 27555 | 17878.5 | 27400 | 155 | 0.5657% | 200 | 355 | 352796 | 1287274 | 3.7798 | 5.3368 | 5336.84 | 442.72 | 0.09 | 33.78 | 39.96 | 70.17% | 66.14% | 5.3126 | 15.75% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 5:35 | 17:45 | 12:10 | 1. Due to Communication Card failure. | 1.Daily Visual inspection. 2.Inspection Done by Scada. 3. 35 nos of table at INV-1.2- Module Cleaning completed 4. ICR-2 All inverters cleaning work completed. 5. ICR-1, INV-1.2, SMB-3-string no-10,13 & SMB-7, String No-13 Solved the problem and now all running, SMB-3, String no-12 +ve string found faulty its need to replace. 6. ICR-2 one AC is not working.
2019-05-16 | 5:34 | 18:16 | 12:42 | 4556 | 4496 | 5277 | 5327 | 4442 | 5639 | 29737 | 17908 | 29500 | 237 | 0.8034% | 200 | 437 | 382533 | 1317011 | 4.0791 | 6.3337 | 6333.67 | 480.29 | 0.07 | 33.36 | 38.96 | 66.87% | 63.29% | 5.7635 | 17% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2 | 1. 05:34:00 2. 14:35:00, 15:15:00 | 1. 18:16:00 2. 14:55:00, 18:16:00 | 1. 12:42:00 2. 03:21:00 | 1. Due to Communication Card failure. 2. Due to temperature alarm at node-3, common fan of node3&4 is not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 35 nos of table at INV-1.2 and INV-1.1- Module Cleaning completed 4. Physical Inspection of UPS, Battery and Battery charger checking completed. all batterys are working. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-17 | 5:35 | 16:23 | 10:48 | 3939 | 3748 | 4398 | 4464 | 2591 | 4747 | 23887 | 17931.7 | 23700 | 187 | 0.789% | 100 | 287 | 406420 | 1340898 | 3.2767 | 5.0471 | 5047.08 | 466.97 | 0.033 | 33.73 | 38.66 | 64.97% | 61.56% | 5.6036 | 13.65% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:35:00 2. 05:35:00 3. 10:15:00 | 1. 16:23:00 2. 16:23:00 3. 16:23:00 | 1. 10:48:00 2. 10:48:00 3. 10:48:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 35 nos of table at INV-1.2 and INV-1.1- Module Cleaning completed 4. Physical Inspection of LT panel checking completed. found all are good condition. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-18 | 5:35 | 18:12 | 12:37 | 4597 | 4209 | 4941 | 5017 | 3999 | 5189 | 27952 | 17959.4 | 27700 | 252 | 0.9097% | 200 | 452 | 434372 | 1368850 | 3.8343 | 5.7558 | 5755.8 | 455.41 | 0.01 | 34.92 | 40.14 | 66.73% | 62.85% | 5.4649 | 15.98% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:35:00 2. 05:35:00 3. 05:35:00 | 1. 18:12:00 2. 18:12:00 3. 18:12:00 | 1. 12:37:00 2. 12:37:00 3. 12:37:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 16 nos of table at INV-INV-1.2- Module Cleaning completed 4. Physical Inspection of RTU & MTU checking completed. found all are good condition. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-19 | 5:34 | 18:08 | 12:34 | 4565 | 4213 | 5015 | 5052 | 4066 | 5341 | 28252 | 17987.4 | 28000 | 252 | 0.9% | 200 | 452 | 462624 | 1397102 | 3.8754 | 5.8015 | 5801.47 | 461.13 | 0.01 | 35.81 | 41.43 | 66.88% | 62.66% | 5.5336 | 16.15% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:34:00 2. 05:34:00 3. 05:34:00 | 1. 18:08:00 2. 18:08:00 3. 18:08:00 | 1. 12:34:00 2. 12:34:00 3. 12:34:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 28 nos of table at INV-INV-1.2 and 1.3- Module Cleaning completed 4. Physical Inspection of weather station checking completed. found all are good condition. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-20 | 5:34 | 17:43 | 12:09 | 4348 | 3996 | 4689 | 4763 | 4014 | 4995 | 26805 | 18014 | 26600 | 205 | 0.7707% | 200 | 405 | 489429 | 1423907 | 3.677 | 5.4149 | 5414.87 | 445.47 | 0.01 | 35.22 | 39.59 | 67.93% | 64.13% | 5.3456 | 15.32% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:34:00 2. 05:34:00 3. 05:34:00 | 1. 17:43:00 2. 17:43:00 3. 17:43:00 | 1. 12:09:00 2. 12:09:00 3. 12:09:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 31 nos of table at INV-1.1 Module Cleaning completed 4. Physical Inspection of Fire Alarm system checking completed. found all are good condition. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-21 | 5:34 | 17:59 | 12:25 | 4521 | 4145 | 4894 | 4964 | 3948 | 5229 | 27701 | 18041.5 | 27500 | 201 | 0.7309% | 200 | 401 | 517130 | 1451608 | 3.7999 | 5.6723 | 5672.34 | 456.05 | 0.01 | 34.49 | 39.1 | 67.1% | 63.47% | 5.4726 | 15.83% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:34:00 2. 05:34:00 3. 05:34:00 | 1. 17:59:00 2. 17:59:00 3. 17:59:00 | 1. 12:25:00 2. 12:25:00 3. 12:25:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 35 nos of table at INV-1.3 Module Cleaning completed 4. Physical Inspection of Street Lights, HT Panel and VCB checking completed. found all are good condition. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-22 | 5:31 | 18:20 | 12:49 | 4504 | 4126 | 4881 | 4927 | 3933 | 5206 | 27577 | 18068.9 | 27400 | 177 | 0.646% | 100 | 277 | 544707 | 1479185 | 3.7829 | 5.7255 | 5725.51 | 442.59 | 0.01 | 34.42 | 39.43 | 66.69% | 62.99% | 5.3111 | 15.76% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 | 1. 05:31:00 2. 05:31:00 3. 05:31:00 | 1. 18:20:00 2. 18:20:00 3. 18:20:00 | 1. 12:49:00 2. 12:49:00 3. 12:49:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 35 nos of table at INV-1.3 Module Cleaning completed 4. Visual Inspection of Street Lights, Aux and ICR-1 Transaformers checking completed. found all Two light was not working and we replaced it. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. INV-1.2, SMB-6, String-2 one MC4 was burned found and replaced, now string is running condition.
2019-05-23 | 5:35 | 18:12 | 12:37 | 4346 | 3975 | 4461 | 4695 | 4284 | 4930 | 26691 | 18095.4 | 26500 | 191 | 0.7208% | 200 | 391 | 571398 | 1505876 | 3.6613 | 5.4051 | 5405.14 | 431.28 | 0.02 | 34.51 | 38.31 | 67.29% | 63.85% | 5.1754 | 15.26% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 4. ICR-1, INV-3 | 1. 05:31:00 2. 05:31:00 3. 05:31:00 4. 07:01:00 | 1. 18:20:00 2. 18:20:00 3. 18:20:00 4. 07:51:00 | 1. 12:49:00 2. 12:49:00 3. 12:49:00 4. 00:51:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. 4. Due to HW & DC protection fault (121) | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 35 nos of table at INV-1.3 & 2.2 Module Cleaning completed. 4. Visual Inspection of Street Lights and ICR-2 Transaformers checking completed. found all Two light was not working and we replaced it. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-24 | 5:54 | 18:14 | 12:20 | 5127 | 4691 | 5640 | 5563 | 4000 | 5837 | 30858 | 18126 | 30600 | 258 | 0.8431% | 200 | 458 | 602256 | 1536734 | 4.2329 | 6.6894 | 6689.4 | 531.46 | 0.04 | 35.96 | 41.7 | 64.58% | 60.44% | 6.3775 | 17.64% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 2. ICR-2, INV-2, Node-3 3. ICR-2, INV-2, Node-4 4. ICR-2, INV-2 | 1. 05:54:00 2. 05:54:00 3. 05:54:00 4. 15:25:00 | 1. 18:14:00 2. 16:56:00 3. 16:56:00 4. 16:56:00 | 1. 12:20:00 2. 11:02:00 3. 11:02:00 4. 01:31:00 | 1. Due to Communication Card failure. 2&3. Due to temperature alarm at node-3, common fan of node3&4 is not working. So from today node -4 also not working. 4. Due to Fan replacement of node-3&4 by imgeteam engineer. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 10 nos structures gruss cutting completed. 4. Visual Inspection of Street Lights and Switch yeard & substation checking completed. 5. ICR-2, INV-2.2 was tripping due to high temperature, after discussion with anil and team, we was removed the top covered of fan and checked&found one common fan of node-3&4 is not working. today solved that problem it i now running. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-25 | 5:31 | 18:14 | 12:43 | 4448 | 4097 | 4939 | 4937 | 5326 | 5192 | 28939 | 18154.7 | 28700 | 239 | 0.781% | 100 | 339 | 631195 | 1565673 | 3.9697 | 5.7784 | 5778.37 | 453.7 | 0.08 | 36.31 | 40.95 | 68.8% | 64.59% | 5.4444 | 16.54% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 1. 05:31:00 | 1. 18:14:00 | 1. 12:43:00 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 39 nos of table at INV-2.2 and INV-2.1- Module Cleaning completed 4. Visual Inspection of Street Lights and Switch yeard & substation checking completed. 5. ICR-1, INV-1.1, string-9 one MC$ was burn due to ground fault, now its replaced and its working good. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-26 | 5:33 | 18:00 | 12:27 | 3730 | 3386 | 3976 | 4162 | 4419 | 4277 | 23950 | 18178.4 | 23700 | 250 | 0.8711% | 200 | 450 | 655145 | 1589623 | 3.2853 | 4.7099 | 4709.92 | 377.83 | 0.3 | 34.39 | 38.54 | 69.84% | 66.21% | 4.534 | 13.69% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 5:33 | 18:00 | 12:27 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 37 nos of table at INV-2.1- Module Cleaning completed 4. Visual Inspection of Street Lights and Switch yeard checking completed. 5. After 14:50 total plant has cloudy. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-27 | 5:36 | 17:57 | 12:21 | 4143 | 3753 | 4489 | 4651 | 4854 | 4685 | 26575 | 18204.8 | 26400 | 175 | 0.7384% | 200 | 375 | 681720 | 1616198 | 3.6454 | 5.185 | 5184.99 | 419.53 | 0.018 | 34.74 | 38.97 | 70.36% | 66.58% | 5.0344 | 15.19% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 5:36 | 17:57 | 12:21 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. 40 nos of table at INV-2.1 & 2.2- Module Cleaning completed 4. Visual Inspection of Street Lights checking completed. 5. Generation low due to cloudy weather. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-28 | 5:26 | 18:15 | 12:49 | 5098 | 4612 | 5487 | 5556 | 6024 | 5841 | 32618 | 18237.2 | 32400 | 218 | 0.8258% | 100 | 318 | 714338 | 1648816 | 4.4743 | 6.3401 | 6340.06 | 494.09 | 0.18 | 34.6 | 39.77 | 70.66% | 66.65% | 5.9291 | 18.64% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 5:26 | 16:15 | 10:49 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. Due to rain All Modules Cleaned. 4. Visual Inspection of RO Plant and LA checking completed. 5. Grass cutting was started today. 15nos table at INV-1.2 completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-29 | 5:34 | 15:56 | 10:22 | 4490 | 4076 | 4839 | 4917 | 5327 | 5188 | 28837 | 18265.8 | 28600 | 237 | 0.7315% | 100 | 337 | 743175 | 1677653 | 3.9557 | 5.5546 | 5554.62 | 535.15 | 0.23 | 33.37 | 39.49 | 71.3% | 67.34% | 6.4218 | 16.48% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5 | 5:34 | 15:56 | 10:22 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. Inspection Done by Scada. 3. Due to rain All Modules Cleaned. 4. Inverters Cleaning at ICR-1 has been completed. 5. 22nos table at INV-1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high.
2019-05-30 | 5:40 | 18:10 | 12:30 | 5094 | 4782 | 3475 | 5842 | 6354 | 5898 | 31445 | 18297 | 31200 | 245 | 0.7562% | 200 | 445 | 774620 | 1709098 | 4.3134 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 17.97% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:40 | 18:10 | 12:30 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. From today morning SCADA is not working due to Gateway-1 problem. 3. Due to rain All Modules Cleaned. 4. Inverters Cleaning at ICR-2 has been completed. 5. 20nos table at INV-1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated from today. 8. LG big LED Monitor 123CM is not working from today. 9. SMB-6&7 com-card was burn due to rain at INV-1.3. 10. UPS supply is not available at RTU, today its proveded.
2019-05-31 | 5:36 | 18:15 | 12:39 | 5171 | 4690 | 3918 | 5645 | 6123 | 5817 | 31364 | 18328.2 | 31200 | 164 | 0.5734% | 200 | 364 | 805984 | 1740462 | 4.3023 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 17.93% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:36 | 18:15 | 12:39 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Inverters Cleaning at ICR-1 has been completed. 5. 22 nos table at INV-1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. SMB-6&7 com-card was burn due to rain at INV-1.3. 10. UPS supply is not available at RTU, today its proveded.
|  |  |  | 129933 | 114748 | 126494 | 143356 | 136520 | 154933 | 805984

## June-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [18 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative June-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | (kWh/kWp) |  |  | W/m2 | (km/h) | (°C) | (°C) | (%) | (%) |  | (%)
2019-06-01 | 5:30 | 18:10 | 12:40 | 3878 | 3517 | 2932 | 4241 | 4582 | 4307 |  | 23457 | 23300 | 157 | 0.6738% | 100 | 257 | 23457 | 1763919 | 3.2177 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.41% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:30 | 18:10 | 12:40 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 1 to 3 all modules, string Current and Voc checking work completed. 5. 19 nos table at INV-1.1 & 1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. SMB-6&7 com-card was burn due to rain at INV-1.3.
2019-06-02 | 5:45 | 17:40 | 11:55 | 3934 | 3594 | 3044 | 4478 | 4824 | 4532 |  | 24406 | 24300 | 106 | 0.4362% | 200 | 306 | 47863 | 1788325 | 3.3479 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.95% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:45 | 17:40 | 11:55 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 4 to 7 all modules, string Current and Voc checking work completed. 5. 15 nos table at INV-1.1 & 1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. SMB-6&7 com-card was burn due to rain at INV-1.3.
2019-06-03 | 5:39 | 17:40 | 12:01 | 1575 | 1425 | 1195 | 1718 | 1857 | 1759 |  | 9529 | 9300 | 229 | 2.462% | 100 | 329 | 57392 | 1797854 | 1.3071 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.446% | 12:30 | 10:50 | 132KV substation trip Grid off due to rain. | 1:40 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:39 | 17:40 | 12:01 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 1 to 3 all modules, string Current and Voc checking work completed. 5. 15 nos table at INV-1.1 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. SMB-6&7 com-card was burn due to rain at INV-1.3.
2019-06-04 | 5:35 | 18:15 | 12:40 | 5190 | 4661 | 3937 | 5625 | 6106 | 5813 |  | 31332 | 31200 | 132 | 0.4231% | 200 | 332 | 88724 | 1829186 | 4.2979 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 17.91% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:35 | 18:15 | 12:40 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 4 to 7 all modules, string Current and Voc checking work completed. 5. 15 nos table at INV-1.1 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9.INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild.
2019-06-05 | 5:35 | 18:17 | 12:42 | 4882 | 4410 | 3697 | 5370 | 5797 | 5488 |  | 29644 | 29500 | 144 | 0.4881% | 100 | 244 | 118368 | 1858830 | 4.0664 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 16.94% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:35 | 18:17 | 12:42 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 5,6 and INV-1.3 SMB-1 all modules, string Current and Voc checking work completed. 5. 18 nos table at INV-1.2 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9.INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild.
2019-06-06 | 6:10 | 18:20 | 12:10 | 1936 | 1760 | 1437 | 1530 | 2276 | 2129 |  | 11068 | 10900 | 168 | 1.541% | 200 | 368 | 129436 | 1869898 | 1.5182 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 6.326% | 1. 08:47:00 2. 09:38:00 3. 09:50:00 | 1. 08:38:00 2. 09:02:00 3. 09:46:00 | 132KV substation trip Grid off due to rain. | 1. 00:09:00 2. 00:36:00 3. 00:04:00 Total- 00:49:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 6:10 | 18:20 | 12:10 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1.3 SMB-2 to 4 all modules, string Current and Voc checking work completed. 5. 15 nos table at INV-1.1 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9.INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild.
2019-06-07 | 5:50 | 18:17 | 12:27 | 4043 | 3667 | 3026 | 4411 | 4759 | 4518 |  | 24424 | 24300 | 124 | 0.5103% | 100 | 224 | 153860 | 1894322 | 3.3503 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.96% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:50 | 18:17 | 12:27 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1.3 SMB-5 to 7 all modules, string Current and Voc checking work completed. 5. 11 nos table at INV-1.1 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1, 11 and SMB-5, String-15 was down due to Modules faulty, SMB-3, String-11 is solved. 11. Grass cutting machine has given starting problem.
2019-06-08 | 6:38 | 18:13 | 11:35 | 3516 | 3199 | 2673 | 3925 | 4220 | 3957 |  | 21490 | 21300 | 190 | 0.892% | 200 | 390 | 175350 | 1915812 | 2.9479 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.28% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 6:38 | 18:13 | 11:35 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2.1 SMB-1 to 3 all modules, string Current and Voc checking work completed. 5. 8 nos table at INV-1.1 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-09 | 6:05 | 18:16 | 12:11 | 4327 | 3930 | 3263 | 3801 | 5086 | 4885 |  | 25292 | 25100 | 192 | 0.7649% | 100 | 292 | 200642 | 1941104 | 3.4694 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.46% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1 | 1 to 3. 06:05 4. 14:05, 14:43. | 1 to 3. 18:16 4. 14:18, 14:56. | 1. 12:11:00 2. 00:26:00 | 1. Due to Communication Card failure. 2. Inverter Contactor fault (121 code). | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2.1 SMB-4 to 6 all modules, string Current and Voc checking work completed. 5. 08 nos table at INV-1.1 & INV-1.3 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-10 | 5:53 | 17:30 | 11:37 | 2328 | 2126 | 1402 | 2557 | 2757 | 2584 |  | 13754 | 13600 | 154 | 1.132% | 200 | 354 | 214396 | 1954858 | 1.8867 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.861% | 18:15 | 17:30 | 132KV substation trip Grid off due to rain. | 00:45:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:53 | 17:30 | 11:37 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2.1 SMB-7 & ICR-1to 2 all modules, string Current and Voc checking work completed. 5. 10 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-11 | 7:18 | 18:13 | 10:55 | 4183 | 3850 | 2552 | 3095 | 4985 | 4779 |  | 23444 | 23300 | 144 | 0.618% | 0 | 144 | 237840 | 1978302 | 3.2159 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.4% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1 | 1 to 3. 07:18 4. 09:56, 10:22. | 1 to 3. 18:13 4. 10:03, 10:26. | 1. 10:55:00 2. 00:11:00 | 1. Due to Communication Card failure. 2. Inverter Contactor fault (121 code). | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2.2 SMB-3 to 5 all modules, string Current and Voc checking work completed. 5. 11 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-12 | 5:51 | 18:11 | 12:20 | 4655 | 4290 | 2869 | 3687 | 5639 | 5368 |  | 26508 | 26300 | 208 | 0.7909% | 100 | 308 | 264348 | 2004810 | 3.6362 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.15% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. | 5:51 | 18:11 | 12:20 | 1. Due to Communication Card failure. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 SMB-6 to 7 & ICR-2 INV-3 SMB-1all modules,string Current and Voc checking work completed. 5. 15 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2 one AC is not working. for that ICR-2 temperature was going high. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-13 | 5:45 | 18:17 | 12:32 | 3521 | 3226 | 2157 | 2677 | 4079 | 3974 |  | 19634 | 19400 | 234 | 1.206% | 200 | 434 | 283982 | 2024444 | 2.6933 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 11.22% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1 | 1 to 3. 05:45 4. 11:16, 12:12. | 1 to 3. 18:17 4. 11:23, 12:16. | 1. 12:32:00 4. 00:11:00 | 1. Due to Communication Card failure. 4. Inverter Contactor fault (121 code). | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-3 SMB-2,3,4 all modules,string Current and Voc checking work completed. 5. 12 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2 one AC is not working previously,Today after talk with Samaya sir do stabilizer bypass,now AC is running condition. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-14 | 5:37 | 17:45 | 12:08 | 4526 | 4173 | 2805 | 3201 | 5440 | 5220 |  | 25365 | 25100 | 265 | 1.056% | 100 | 365 | 309347 | 2049809 | 3.4794 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.5% | 11:44 | 11:39 | Grid Off due to over voltage | 0:05 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1. 5. ICR-2, INV-1, Node-3. 6. ICR-1 and ICR-2. | 1to3. 05:45 4. 10:40, 11:55 5. 12:05. 6. 17:24. | 1to3. 18:17 4. 11:15, 12:05. 5. 17:45. 6. 17:26. | 1to3. 12:32:00 4. 00:50:00 5. 05:40:00 6. 00:02:00 | 1 to 3 Due to communication card failure. 4.Inverter contactor fault(121)code. 5.Due to high temparature (110 code) node-3 was off. 6.Due to MFM meter change its take 2min shut down. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-3 SMB-5,6,7 all modules,string Current and Voc checking work completed. 5. 11 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue, its given alarm every 10min and total inverter was going trip. so after discuss with anil we was off that Node-3 and start the Inverter and after that inv -2.1 was running properly. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. For SLD communication 2 person came at side and they was changed old MFM meter with new one At Incomer-1 & 2. Also new MFM was connected at Incomer- 3 & 4.
2019-06-15 | 5:43 | 18:37 | 12:54 | 4785 | 4443 | 2953 | 4334 | 5796 | 5565 |  | 27876 | 27700 | 176 | 0.6354% | 200 | 376 | 337223 | 2077685 | 3.8239 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.93% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 5:43 | 18:37 | 12:54 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1,2,3 inverter cleaning work completed. 5. 12 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue, its given alarm every 10min and total inverter was going trip. so after discuss with anil we was off that Node-3 and start the Inverter and after that inv -2.1 was running properly. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem.
2019-06-16 | 6:21 | 17:35 | 11:14 | 2168 | 1989 | 1299 | 2005 | 2560 | 2398 |  | 12419 | 12200 | 219 | 1.795% | 100 | 319 | 349642 | 2090104 | 1.7036 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.098% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 6:21 | 17:35 | 11:14 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1,2,3 inverter cleaning work completed. 5. 20 nos table at INV-1.3 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue, its given alarm every 10min and total inverter was going trip. so after discuss with anil we was off that Node-3 and start the Inverter and after that inv -2.1 was running properly. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 10 no Earthpit value checking completed. 13. All Lightning Arrester checking completed.
2019-06-17 | 5:43 | 18:31 | 12:48 | 4382 | 4016 | 2671 | 4026 | 5287 | 4894 |  | 25276 | 25000 | 276 | 1.104% | 200 | 476 | 374918 | 2115380 | 3.4672 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.45% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 5:43 | 18:31 | 12:48 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically inspection of UPS,Battery &Battery charger checking completed. 5. 12 nos table at INV-2.2 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue, its given alarm every 10min and total inverter was going trip. so after discuss with anil we was off that Node-3 and start the Inverter and after that inv -2.1 was running properly.but Node-3 fan not working. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 10 no Earthpit value checking completed.
2019-06-18 | 5:45 | 18:05 | 12:20 | 1279 | 1170 | 752 | 1212 | 1550 | 1399 |  | 7362 | 7300 | 62 | 0.8493% | 100 | 162 | 382280 | 2122742 | 1.0099 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 4.208% | 1. 11:22:00 2. 18:05:00 | 1. 11:00:00 2. 11:40:00 | Grid Off, LC taken due to CT's and meters replacement work. | 1. 00:22:00 2. 06:25:00 Total= 06:47:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 5:45 | 18:05 | 12:20 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically LT panel cleaning completed. 5. 12 nos table at INV-2.2 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue, its given alarm every 10min and total inverter was going trip. so after discuss with anil we was off that Node-3 and start the Inverter and after that inv -2.1 was running properly.but Node-3 fan not working. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 10 no Earthpit value checking completed. 13.Grid of 11:40 due to Meters and CT replacement both side.
2019-06-19 | 5:45 | 18:20 | 12:35 | 121 | 10 | 73 | 80 | 133 | 78 | 250 | 745 | 700 | 45 | 6.429% | 0 | 45 | 383025 | 2123487 | 0.10219 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0.4258% | 16:10 | 5:45 | Grid Off, LC taken due to CT's and meters replacement work. | 10:25 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 5:45 | 18:20 | 12:35 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically RTU and MTU checking completed. 5. 10 nos table at INV-2.2 Grass cutting has completed. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem, Fan was not working at node -3. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 05 no Earthpit value checking completed. 13.Grid off, LC was taken from yesterday to today 16:10, due to Meters and CT replacement at substation and switchyard both side. 14. From today New 3 MWp was start, that generation also add in main meters.
2019-06-20 | 5:47 | 18:28 | 12:41 | 2175 | 1997 | 1309 | 1995 | 2568 | 2404 | 5690 | 18138 | 17900 | 238 | 1.33% | 200 | 438 | 401163 | 2141625 | 2.4881 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 10.37% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. | 5:47 | 18:28 | 12:41 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically Weather station checking completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem, Fan was not working at node -3. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 05 no Earthpit value checking completed. 13. From 19th june-2019 New 3 MWp plant was start, that generation also add in main meters.
2019-06-21 | 5:45 | 18:20 | 12:35 | 717 | 2887 | 2031 | 3033 | 4028 | 3784 | 8900 | 25380 | 25300 | 80 | 0.3162% | 100 | 180 | 426543 | 2167005 | 2.4665 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.51% | 1. 06:30:00 2. 18:20:00 | 1. 05:45:00 2. 16:40:00 | Grid Off due to Rain, AC braker was trip at SS | 1. 00:45:00 2. 01:40:00 Total= 02:25:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1. 7. ICR-1, INV-2. | 1 to 5. 05:45:00 6. 05:45:00 7. 09:10:00 | 1 to 5. 18:20:00 6. 09:30:00 7. 09:40:00 | 1 to 5. 12:35:00 6. 03:45:00 7. 00:30:00 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5 to 7. Ground fault due to heavy rain. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically Fire alarm and battery checking completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.2. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem, Fan was not working at node -3. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 22 nos Street light checking completed and its working. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. From 19th june-2019 New 3 MWp plant was start, that generation also add in main meters.
2019-06-22 | 6:05 | 18:10 | 12:05 | 0 | 0 | 0 | 861 | 1112 | 1038 | 2560 | 5571 | 5400 | 171 | 3.167% | 0 | 171 | 432114 | 2172576 | 0.5414 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 3.184% | 1. 09:50:00 2. 11:45:00 | 1. 06:05:00 2. 11:00:00 | Grid Off due to Rain, AC braker was trip at SS | 1. 03:45:00 2. 00:45:00 Total= 04:30:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 6:05 | 18:10 | 12:05 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel and VCB checking completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.2. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. Today one service engineer come from LG and told motherboard was faulty need to replaced, after 4days it will come then he will come at site and replaced. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 22 nos Street light checking completed and its working. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. power Transformer at ICR-1 has found some problem at LV side, megger value of LV side not good, ICR-1 full day down.
2019-06-23 | 5:52 | 18:15 | 12:23 | 0 | 0 | 0 | 3816 | 4942 | 4675 | 11360 | 24793 | 24500 | 293 | 1.196% | 100 | 393 | 456907 | 2197369 | 2.4094 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.17% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:52 | 18:15 | 12:23 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel and VCB checking completed at ICR-1. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.1. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. One service engineer come from LG and told motherboard was faulty need to replaced, after 26th it will come then he will come at site and replaced. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 22 nos Street light checking completed and its working. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. power Transformer at ICR-1 has found some problem at LV side, megger value of LV side not good, ICR-1 full day down. HV side checked and megger completed, all value coming good.
2019-06-24 | 5:49 | 18:36 | 12:47 | 0 | 0 | 0 | 4024 | 5296 | 5005 | 12140 | 26465 | 26300 | 165 | 0.6274% | 200 | 365 | 483372 | 2223834 | 2.5719 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.13% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:49 | 18:36 | 12:47 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel and VCB checking completed at ICR-2. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.1. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. One service engineer come from LG and told motherboard was faulty need to replaced, after 26th it will come then he will come at site and replaced. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. Grass cutting machine has given starting problem. 12. 22 nos Street light checking completed At new plant and its working. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. power Transformer at ICR-1 has found some problem at LV side, tomorrow transformer team will come for testing.
2019-06-25 | 5:46 | 18:40 | 12:54 | 0 | 0 | 0 | 4338 | 5638 | 5362 | 13310 | 28648 | 28400 | 248 | 0.8732% | 100 | 348 | 512020 | 2252482 | 2.7841 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 16.37% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:46 | 18:40 | 12:54 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is not working due to Gateway-1 problem. today found some problem in GW-2 & some SPD. 3. Due to rain All Modules Cleaned. 4. Routine inspection of power transformer(ICR-1) completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.1. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. One service engineer come from LG and told motherboard was faulty need to replaced, after 26th it will come then he will come at site and replaced. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 13. 22 nos Street light checking completed At new plant and its working. 14. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 15. power Transformer at ICR-1 has failed need to send Hyd workshop, today transformer person was come for testing.
2019-06-26 | 5:46 | 18:55 | 13:09 | 0 | 0 | 0 | 5039 | 6521 | 6114 | 14786 | 32460 | 32300 | 160 | 0.4954% | 100 | 260 | 544480 | 2284942 | 3.1545 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 18.55% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:46 | 18:55 | 13:09 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is working, SPDs are good, but both gateway had change at MCR. 3. Due to rain All Modules Cleaned. 4. Routine inspection of power transformer(ICR-2) not completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. Cable dressing work done at INV-1.1. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated . 8. LG big LED Monitor not working. One service engineer come from LG and told motherboard was faulty need to replaced, after 26th it will come then he will come at site and replaced, no response. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 14. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 15. power Transformer at ICR-1 has failed need to send Hyd workshop, so removed oil and LV and HV side. 16. New plant MCR feeder control panel and MFM power connection come from LT panel-2, but today morning 1hr that power trip and there havent any UPS connection, so 1606KWh was miss from New plant MFM.
2019-06-27 | 5:28 | 18:39 | 13:11 | 0 | 0 | 0 | 4656 | 6040 | 5696 | 13840 | 30232 | 30100 | 132 | 0.4385% | 200 | 332 | 574712 | 2315174 | 2.938 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 17.28% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:28 | 18:39 | 13:11 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. SCADA is working, SPDs are good, but both gateway had change at MCR. 3. Due to rain All Modules Cleaned. 4. Routine inspection completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated. 8. LG big LED Monitor not working. One service engineer come from LG and told motherboard was faulty need to replaced, after 26th it will come then he will come at site and replaced, no response. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 14. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 15. power Transformer at ICR-1 has failed need to send Hyd workshop, so removed oil and LV and HV side. 16. team are involved transformer unloading and loading for full day. no schdule work completed.
2019-06-28 | 5:32 | 18:25 | 12:53 | 0 | 0 | 0 | 3771 | 4872 | 4581 | 11160 | 24384 | 24100 | 284 | 1.178% | 100 | 384 | 599096 | 2339558 | 2.3697 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.94% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:32 | 18:25 | 12:53 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine inspection completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated. 8. LG big LED Monitor is start working, After change 1 PCB by LG person. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 14. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 15. team are involved transformer unloading and loading for full day. no schdule work completed.
1900-01-28 | 5:32 | 18:37 | 13:05 | 0 | 0 | 0 | 3234 | 4159 | 3881 | 9570 | 20844 | 20700 | 144 | 0.6957% | 200 | 344 | 619940 | 2360402 | 2.0257 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 11.91% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:32 | 18:37 | 13:05 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine inspection of RO plant checking completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated. 8. LG big LED Monitor is start working, After change 1 PCB by LG person. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. Today HT testing team come at site.
2019-06-30 | 5:35 | 18:24 | 12:49 | 0 | 0 | 0 | 1953 | 2513 | 2336 | 6060 | 12862 | 12700 | 162 | 1.276% | 100 | 262 | 632802 | 2373264 | 1.25 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.351% |  |  |  | 0:00 | 1. ICR-1, INV-2, SMB-5. 2. ICR-1, INV-3, SMB-6, 3. ICR-1, INV-3, SMB-7. 4. ICR-2, INV-1, Node-3. 5. INV-1.1, SMB-3,4&7. 6. ICR-1, INV-1, 2 & 3. | 5:35 | 18:24 | 12:49 | 1 to 3 Due to communication card failure. 4.Due to high temparature (110 code) node-3 was off. 5. Ground fault due to heavy rain. 6. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine inspection of Lightening Arrestors checking completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated. 8. LG big LED Monitor is start working, After change 1 PCB by LG person. 9. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 10. INV-1.3, SMB-3, String -1 and SMB-5, String-15 was down due to Modules faulty. 11. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 12. Grass cutting machine has given starting problem. 13. AT INV-1.1 and INV-1.2 some SMB have problem and it was down due to ground fault. 14. Yesterday HT testing team come at site,today also testing continue.
|  |  |  | 68121 | 64340 | 48077 | 98693 | 125422 | 118523 |  | 632802

## July-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [18 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative July-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | (kWh/kWp) |  |  | W/m2 | (km/h) | (°C) | (°C) | (%) | (%) |  | (%)
2019-07-01 | 5:35 | 18:21 | 12:46 | 0 | 0 | 0 | 2309 | 2970 | 2772 | 7040 | 15091 | 14900 | 191 | 1.282% | 100 | 291 | 15091 | 2388355 | 1.4666 | #VALUE! | [5 empty] | #DIV/0! | #DIV/0! | 0 | 8.625% |  |  |  | 0:00 | 1. ICR-2, INV-1, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:35 | 18:21 | 12:46 | 1.Due to high temparature (110 code) node-3 was off. 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 1 to 3 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated.. 8. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 9. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 10. Grass cutting machine has given starting problem.
2019-07-02 | 5:42 | 18:15 | 12:33 | 0 | 0 | 0 | 2130 | 2743 | 2551 | 6330 | 13754 | 13600 | 154 | 1.132% | 100 | 254 | 28845 | 2402109 | 1.3366 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.861% |  |  |  | 0:00 | 1. ICR-2, INV-1, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:42 | 18:15 | 12:33 | 1.Due to high temparature (110 code) node-3 was off. 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 4 to 6 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated.. 8. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 9. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 10. Grass cutting machine has given starting problem.
2019-07-03 | 5:36 | 18:10 | 12:34 | 0 | 0 | 0 | 1793 | 2339 | 1830 | 5480 | 11442 | 11300 | 142 | 1.257% | 200 | 342 | 40287 | 2413551 | 1.112 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 6.54% |  |  |  | 0:00 | 1. ICR-2, INV-1, Node-3. 2. ICR-1, INV-1, 2 & 3. 3. ICR-2, INV-1 | 1&2. 05:36:00 3. 16:20:00 | 1&2. 18:10:00 3. 18:10:00 | 1&2. 12:34:00 3. 01:50:00 | 1.Due to high temparature (110 code) node-3 was off. 2. Transformer Oil level fail and smoke observed from common neutral bushing. 3. Down due to fan changed at node-3 | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 7 & Inv-2 SMB-1,2 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. ICR-2, INV-1, Node-3 have temparature issue due to Fan problem. 7. TCP card's of inv-1.3 is not working, so INV-1.3 not communicated.. 8. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 9. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 10. Grass cutting machine has given starting problem.
2019-07-04 | 5:35 | 18:15 | 12:40 | 0 | 0 | 0 | 3422 | 4427 | 3708 | 10310 | 21867 | 21600 | 267 | 1.236% | 100 | 367 | 62154 | 2435418 | 2.1251 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.5% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-2. 2. ICR-1, INV-1, 2 & 3. | 5:35 | 18:15 | 12:40 | 1.Due to PI. SAT. (116) node-2 at INV-2.3 was down. 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 3 to 5 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-2 down due to PI. SAT.(116) 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-05 | 5:46 | 18:05 | 12:19 | 0 | 0 | 0 | 1818 | 2337 | 2177 | 5490 | 11822 | 11700 | 122 | 1.043% | 200 | 322 | 73976 | 2447240 | 1.1489 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 6.757% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-2. 2. ICR-1, INV-1, 2 & 3. | 5:46 | 18:05 | 12:19 | 1.Due to PI. SAT. (116) node-2 at INV-2.3 was down. 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 6,7 and INV-3 SMB1 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-2 down due to PI. SAT.(116) 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-06 | 5:38 | 18:25 | 12:47 | 0 | 0 | 0 | 1366 | 1752 | 1602 | 4090 | 8810 | 8600 | 210 | 2.442% | 100 | 310 | 82786 | 2456050 | 0.85617 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.035% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-2. 2. ICR-1, INV-1, 2 & 3. | 5:38 | 18:25 | 12:47 | 1.Due to PI. SAT. (116) node-2 at INV-2.3 was down. 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-3 SMB2 to 4 all modules, string Current and Voc checking work not completed due to rain. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-2 down due to PI. SAT.(116), today interchange the conductor with node3 and now node 3 is down, and from tomorrow node-2 will running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-07 | 5:34 | 18:25 | 12:51 | 0 | 0 | 0 | 3638 | 4620 | 4194 | 10810 | 23262 | 23100 | 162 | 0.7013% | 200 | 362 | 106048 | 2479312 | 2.2606 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.3% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:34 | 18:25 | 12:51 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-3 SMB 5 to 7 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-08 | 5:32 | 18:20 | 12:48 | 0 | 0 | 0 | 4125 | 5337 | 4816 | 12690 | 26968 | 26700 | 268 | 1.004% | 100 | 368 | 133016 | 2506280 | 2.6208 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.41% | 16:48 | 16:40 | Grid fail at SS | 0:08 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:32 | 18:20 | 12:48 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1 SMB 1 to 3 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 9. New 3 MW plant take shoutdown by MSPL from 17:40 due to closing punch points.
2019-07-09 | 5:42 | 18:15 | 12:33 | 0 | 0 | 0 | 3820 | 4719 | 4217 | 10915 | 23671 | 23500 | 171 | 0.7277% | 200 | 371 | 156687 | 2529951 | 2.3004 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.53% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:42 | 18:15 | 12:33 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1 SMB 4 to 6 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 9. MCR float and boost charger showing earth fault and its now clear. 10. New plant MCR feeder control panel and MFM power connection come from LT panel-2, but today morning 1hr that power trip and there havent any UPS connection, so 335KWh was miss from New plant MFM.
2019-07-10 | 5:38 | 18:25 | 12:47 | 0 | 0 | 0 | 3877 | 4218 | 3872 | 9870 | 21837 | 21600 | 237 | 1.097% | 100 | 337 | 178524 | 2551788 | 2.1222 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.48% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:38 | 18:25 | 12:47 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1 SMB 7, INV-2 SMB-1&2 all modules, string Current and Voc checking work completed. 5. INV-2.2 Grass cutting has not completed due to machine problem.20 table manual grass cutting completed. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-11 | 5:39 | 18:25 | 12:46 | 0 | 0 | 0 | 4733 | 5139 | 4766 | 12300 | 26938 | 26800 | 138 | 0.5149% | 200 | 338 | 205462 | 2578726 | 2.6179 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.4% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:39 | 18:25 | 12:46 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 SMB-3 to 5 all modules, string Current and Voc checking work completed. 5. INV-2.2, 15 table grass cutting completed, machine repair today. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-12 | 5:33 | 18:25 | 12:52 | 0 | 0 | 0 | 4811 | 5249 | 4800 | 12550 | 27410 | 27100 | 310 | 1.144% | 100 | 410 | 232872 | 2606136 | 2.6638 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.67% | 8:18 | 7:40 | Grid fail at SS | 0:38 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:33 | 18:25 | 12:52 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 SMB-6,7 and INV-3 SMB-1 all modules, string Current and Voc checking work completed. 5. INV-2.2, 20 table grass cutting completed. 6. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-13 | 5:35 | 18:10 | 12:35 | 0 | 0 | 0 | 3664 | 3962 | 3679 | 9270 | 20575 | 20400 | 175 | 0.8578% | 200 | 375 | 253447 | 2626711 | 1.9995 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 11.76% | 15:02 | 14:33 | Grid fail at SS Due to Rain | 0:29 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:35 | 18:10 | 12:35 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-3 SMB-2 to 4 all modules, string Current and Voc checking work completed. 5. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity.
2019-07-14 | 5:35 | 18:25 | 12:50 | 0 | 0 | 0 | 3861 | 4139 | 3740 | 9490 | 21230 | 21100 | 130 | 0.6161% | 100 | 230 | 274677 | 2647941 | 2.0632 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.13% | 12:50 | 12:03 | Grid fail | 0:47 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. 3. Outgoing VCB | 1&2. 05:35:00 3. 16:35:00 | 1&2. 18:25:00 3. 16:36:00 | 1&2. 12:50:00 3. 00:01:00 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2. 2. Transformer Oil level fail and smoke observed from common neutral bushing. 3. Due to over incoming voltage VCB was trip. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-3 SMB-5 to 7 all modules, string Current and Voc checking work completed. 5. INV-2.3 Node-3 down due to PI. SAT.(116), After interchange the conductor with node3 and now node 3 is down, and node-2 is running. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. INV-2.2, 16 table grass cutting completed.
2019-07-15 | 5:36 | 18:00 | 12:24 | 0 | 0 | 0 | 4380 | 4691 | 4330 | 10920 | 24321 | 24000 | 321 | 1.337% | 200 | 521 | 298998 | 2672262 | 2.3636 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.9% |  |  |  | 0:00 | 1. ICR-2, INV-3, Node-3. 2. ICR-1, INV-1, 2 & 3. | 5:36 | 18:00 | 12:24 | 1.Due to PI. SAT. (116) node-3 at INV-2.3 was down. after Interchanged conductor with nde-2 2. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1, INV-1,2&3 cleaning completed. 5. INV-2.3 Node-2 was replaced with new conductor and node-3 had connected own old conductor, and now node 3 and node-2 is running. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. INV-2.1, 15 table grass cutting completed.
2019-07-16 | 5:33 | 18:25 | 12:52 | 0 | 0 | 0 | 5786 | 6198 | 5780 | 14280 | 32044 | 31800 | 244 | 0.7673% | 200 | 444 | 331042 | 2704306 | 3.1141 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 18.32% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. | 5:33 | 18:25 | 12:52 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2, INV-1,2&3 cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. INV-2.1, 15 table grass cutting completed. 8. Power is not available, so DGR not completed today.
2019-07-17 | 5:34 | 18:25 | 12:51 | 0 | 0 | 0 | 3905 | 4202 | 3946 | 9580 | 21633 | 21500 | 133 | 0.6186% | 100 | 233 | 352675 | 2725939 | 2.1023 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.36% | 08:10, 16:14, 17:12. | 7:42, 15:37, 17:06. | Grid fail | 1:11 | 1. ICR-1, INV-1, 2 & 3. | 5:34 | 18:25 | 12:51 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of UPS, Battery and Battery Chargers completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. INV-2.1, 15 table grass cutting completed. 8. ICR-2 SCADA was checked by neosillica and found gateway-1 RS485 port was damaged.
2019-07-18 | 5:39 | 17:55 | 12:16 | 0 | 0 | 0 | 4961 | 5272 | 4956 | 10040 | 25229 | 25100 | 129 | 0.5139% | 100 | 229 | 377904 | 2751168 | 2.4518 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.42% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. | 5:39 | 17:55 | 12:16 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of LT panel & Earthpit checking (ICR -1,2 & MCR) completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. INV-2.1, 20 table grass cutting completed. 8. Grass cutting machine starter not working.
2019-07-19 | 5:41 | 18:25 | 12:44 | 0 | 0 | 0 | 2059 | 2181 | 1844 | 4950 | 11034 | 10800 | 234 | 2.167% | 200 | 434 | 388938 | 2762202 | 1.0723 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 6.307% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. | 5:41 | 18:25 | 12:44 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of RTU&MTU & Earthpit checking (ICR -2 Structure) completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. INV-2.1, 25 table grass cutting completed manually. 8. Grass cutting machine starter not working. 9. Trasnformer oil (ICR-1) taken by Esenner team.
2019-07-20 | 5:37 | 18:30 | 12:53 | 0 | 0 | 0 | 3536 | 3420 | 3281 | 8610 | 18847 | 18700 | 147 | 0.7861% | 200 | 347 | 407785 | 2781049 | 1.8316 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 10.77% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-2. 3..ICR-2,INV-2,NODE-2. | 1.05:37 2.11:48 3.12:00 | 1.18:30 2.11:55 3.18:30 | 1.12:53:00 2.00:07:00 3.06:30:00 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Inverter contactor fault(121 code). 3.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of Weather Station & Earthpit checking (LA Structure) completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. INV-2.2, 30 table grass cutting completed manually. 8. Grass cutting machine starter not working. 9. ICR-2,INV-2,NODE-2 off due to116 PI SATE error.
2019-07-21 | 5:33 | 18:24 | 12:51 | 0 | 0 | 0 | 4637 | 4848 | 4699 | 11600 | 25784 | 25500 | 284 | 1.114% | 200 | 484 | 433569 | 2806833 | 2.5057 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.74% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-2.. | 1&2.05:33 | 1&2.18:24 | 12:51 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of Fire Detector & Street Light(1 to 21) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-2,INV-2,NODE-2 off due to116 PI SATE error.
2019-07-22 | 5:38 | 18:25 | 12:47 | 0 | 0 | 0 | 4767 | 4978 | 4749 | 11540 | 26034 | 25900 | 134 | 0.5174% | 200 | 334 | 459603 | 2832867 | 2.53 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.88% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-2.. | 5:38 | 18:25 | 12:47 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of HT panel and VCB cleaning & Street Light(22 to 44) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-2.3, 30 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 off due to116 PI SATE error. We are replaced conductor between node-1 and node-2 properly, but due to low irradiation we cannt test, tomorrow morning we are test. now all node are on condition.
2019-07-23 | 5:35 | 18:25 | 12:50 | 0 | 0 | 0 | 5230 | 5132 | 5109 | 12330 | 27801 | 27500 | 301 | 1.095% | 100 | 401 | 487404 | 2860668 | 2.7017 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.89% | 16:56 | 16:50 | Grid fail | 0:06 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-1.. | 5:35 | 18:25 | 12:50 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of HT panel and VCB cleaning (ICR-1) & Street Light(45 to 66) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-2.3, 30 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 off due to116 PI. SAT. error. We are replaced conductor between node-1 and node-2 properly, but Now node-1 was showing PI. SAT. so, Node-1 is off condition and node-2 is running.
2019-07-24 | 5:40 | 18:10 | 12:30 | 0 | 0 | 0 | 4758 | 4835 | 4898 | 11580 | 26071 | 25800 | 271 | 1.05% | 200 | 471 | 513475 | 2886739 | 2.5336 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.9% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-1.. | 5:40 | 18:10 | 12:30 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of HT panel and VCB cleaning (ICR-2) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-2.3, 21 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 off due to116 PI. SAT. error. We are replaced conductor between node-1 and node-2 properly, but Now node-1 was showing PI. SAT. so, Node-1 is off condition and node-2 is running.
2019-07-25 | 5:45 | 18:15 | 12:30 | 0 | 0 | 0 | 2774 | 2992 | 2830 | 6600 | 15196 | 15100 | 96 | 0.6358% | 100 | 196 | 528671 | 2901935 | 1.4768 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 8.685% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-1.. | 5:45 | 18:15 | 12:30 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of street light (67 to 88) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.1, 30 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 off due to116 PI. SAT. error. We are replaced conductor between node-1 and node-2 properly, but Now node-1 was showing PI. SAT. so, Node-1 is off condition and node-2 is running.
2019-07-26 | 5:54 | 18:10 | 12:16 | 0 | 0 | 0 | 1499 | 1614 | 1526 | 3450 | 8089 | 7900 | 189 | 2.392% | 200 | 389 | 536760 | 2910024 | 0.7861 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 4.623% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-1.. | 5:54 | 18:10 | 12:16 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of Trasnformer(ICR-2) and street light (89 to 120) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.1, 25 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 off due to116 PI. SAT. error. We are replaced conductor between node-1 and node-2 properly, but Now node-1 was showing PI. SAT. so, Node-1 is off condition and node-2 is running. 10. new 3 mW plant, inv-5 was damaged due to internal fault. 11. yesterday we were checking tighten of 1.5MVA transformer for oil leakage.
2019-07-27 | 5:44 | 18:18 | 12:34 | 0 | 0 | 0 | 2495 | 2684 | 2529 | 5850 | 13558 | 13500 | 58 | 0.4296% | 200 | 258 | 550318 | 2923582 | 1.3176 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.749% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. 2.ICR-2,INV-2,NODE-1.. | 5:44 | 18:18 | 12:34 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Due to 116 PI SATE error. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of SCADA and street light (121to 149 ) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.2, 25 table grass cutting completed manually. 9. ICR-2,INV-2,NODE-2 Contactor changing completed. 10. new 3 mW plant, inv-5 was damaged due to internal fault.
2019-07-28 | 5:46 | 18:14 | 12:28 | 0 | 0 | 0 | 1261 | 1352 | 1276 | 2920 | 6809 | 6600 | 209 | 3.167% | 100 | 309 | 557127 | 2930391 | 0.66171 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 3.892% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. | 5:46 | 18:14 | 12:28 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of HT switch yard checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault.
2019-07-29 | 5:45 | 18:27 | 12:42 | 0 | 0 | 0 | 2724 | 2934 | 2762 | 6270 | 14690 | 14600 | 90 | 0.6164% | 200 | 290 | 571817 | 2945081 | 1.4276 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 8.396% | 14:26 | 14:32 | Grid fail | 0:06 | 1. ICR-1, INV-1, 2 & 3. | 5:45 | 18:27 | 12:42 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of RO plant checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.2 , 25 nos table grass cutting completed manually. 9.. new 3 mW plant, inv-5 was damaged due to internal fault. Today service engineer come and check.
2019-07-30 | 5:40 | 18:25 | 12:45 | 0 | 0 | 0 | 5101 | 5527 | 5311 | 11990 | 27929 | 27700 | 229 | 0.8267% | 200 | 429 | 599746 | 2973010 | 2.7142 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.96% |  |  |  | 0:00 | 1. ICR-1, INV-1, 2 & 3. | 5:40 | 18:25 | 12:45 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Physical Inspection of LA checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.2 , 29 nos table grass cutting completed manually. 9.. new 3 mW plant, inv-5 was damaged due to internal fault.
2019-07-31 | 5:41 | 18:06 | 12:25 | 0 | 0 | 0 | 3598 | 5048 | 4816 | 11130 | 24592 | 24300 | 292 | 1.202% | 100 | 392 | 624338 | 2997602 | 2.3899 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.06% | 17:31 | 17:47 | Grid fail | 0:16 | 1. ICR-1, INV-1, 2 & 3. 2. ICR 2 INV 1 | 1. 05:41:00 2. 12:38:00 | 1. 18:06:00 2. 12:59:00 | 1. 12:25:00 2. 00:21:00 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2. 121 Contactor fail. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Due to rain some module chacking work was pending, today completed that work. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.1 , 31 nos table grass cutting completed manually. 9. new 3 mW plant, inv-5 was damaged due to internal fault.

## Aug-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [18 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Aug-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | (kWh/kWp) |  |  | W/m2 | (km/h) | (°C) | (°C) | (%) | (%) |  | (%)
2019-08-01 | 5:41 | 18:03 | 12:22 | 0 | 0 | 0 | 2776 | 3605 | 3685 | 8370 | 18436 | 18300 | 136 | 0.7432% | 200 | 336 | 18436 | 3016038 | 1.7916 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 10.54% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2. ICR-2, INV-1. 3. ICR-2, INV-2. | 1. 05:41:00 2. 13:30:00 3. 16:10:00 | 1. 18:03:00 2. 15:40:00 3. 17:34:00 | 1. 12:22:00 2. 02:10:00 3. 01:24:00 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2&3. Inv checking by ingeteam engineer. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 SMB 1 to 7 all modules, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.3, 35 nos table grass cutting completed manually. 9. new 3 mW plant, inv-5 was damaged due to internal fault. 10. ICR-2 INV-1 RTM relay bypass completed by Ingeteam Engineer due to Contarcor fail(121).
2019-08-02 | 5:49 | 18:25 | 12:36 | 0 | 0 | 0 | 3237 | 3534 | 2922 | 7630 | 17323 | 17100 | 223 | 1.304% | 200 | 423 | 35759 | 3033361 | 1.6835 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.901% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2. ICR-2, INV-1. 3. ICR-2, INV-3. 4. ICR-2,INV-3. | 1. 05:49:00 2. 11:29:00 3. 11:29:00 4. 12:39:00 | 1. 18:25:00 2. 11:39:00 3. 11:41:00 4. 13:26:00 | 1. 12:36:00 2. 00:10:00 3. 00:12:00 4. 00:47:00 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2&3. Inv checking by ingeteam engineer. 4.Inverter contactor fault(121 code). | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 SMB 1 to 7 all modules, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.3, 25 nos table grass cutting completed manually. 9. new 3 mW plant, inv-5 was damaged due to internal fault. 10. ICR-2 INV-3 RTM relay bypass completed by Ingeteam Engineer due to Contarcor fail(121).
2019-08-03 | 05;52 | 18:08 | 12:16 | 0 | 0 | 0 | 1173 | 1268 | 1195 | 2690 | 6326 | 6300 | 26 | 0.4127% | 100 | 126 | 42085 | 3039687 | 0.61477 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 3.616% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:52 | 18:08 | 12:16 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-3 SMB 1 to 7 all modules, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. INV-1.3, 20 nos table grass cutting completed manually. 9. new 3 mW plant, inv-5 was damaged due to internal fault.
2019-08-04 | 5:45 | 17;58 | 12:13 | 0 | 0 | 0 | 3581 | 3672 | 3706 | 8000 | 18959 | 18700 | 259 | 1.385% | 200 | 459 | 61044 | 3058646 | 1.8425 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 10.84% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:45 | 17:58 | 12:13 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1 SMB 1 to 7 all modules, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged.
2019-08-05 | 5:46 | 18:25 | 12:39 | 0 | 0 | 0 | 3750 | 4017 | 3844 | 8000 | 19611 | 19500 | 111 | 0.5692% | 200 | 311 | 80655 | 3078257 | 1.9058 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 11.21% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:46 | 18:25 | 12:39 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 SMB 1 to 7 all modules, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. INV-1.3, 19 nos table grass cutting completed manually.
2019-08-06 | 5:55 | 18:04 | 12:09 | 0 | 0 | 0 | 1020 | 1107 | 1032 | 2120 | 5279 | 5100 | 179 | 3.51% | 200 | 379 | 85934 | 3083536 | 0.51302 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 3.017% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:55 | 18:04 | 12:09 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 SMB 1 to 7 all modules, string Current and Voc checking work not completed due to rain. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. INV-1.3, 20 nos table grass cutting completed manually.
2019-08-07 | 6:06 | 18:10 | 12:04 | 0 | 0 | 0 | 1206 | 1299 | 1214 | 2510 | 6229 | 6100 | 129 | 2.115% | 200 | 329 | 92163 | 3089765 | 0.60534 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 3.56% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 6:06 | 18:10 | 12:04 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1, INV-1,2&3 cleaning completed. INV-2.3 SMB's checking pending due to rain. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. grass cutting not completed manually due to rain.
2019-08-08 | 5:40 | 18:15 | 12:35 | 0 | 0 | 0 | 1878 | 2046 | 1868 | 3940 | 9732 | 9600 | 132 | 1.375% | 200 | 332 | 101895 | 3099497 | 0.94577 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.562% | 16:38 | 13:33 | Substation bracker issue. | 3:05 | 1. ICR-1, INV-1,2&3 | 5:40 | 18:15 | 12:35 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2, INV-1,2&3 cleaning completed. INV-2.3 SMB's checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. ICR-2, 30 nos table grass cutting completed manually.
2019-08-09 | 5:41 | 18:15 | 12:34 | 0 | 0 | 0 | 2581 | 2777 | 2548 | 5370 | 13276 | 13100 | 176 | 1.344% | 200 | 376 | 115171 | 3112773 | 1.2902 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.588% | 12:25 | 6:48 | LC for line trees cutting | 5:37 | 1. ICR-1, INV-1,2&3 | 5:41 | 18:15 | 12:34 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. All UPS and batteries checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. new 3 mW plant, inv-5 was damaged due to internal fault. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. ICR-2, 31 nos table grass cutting completed manually. 11. Overhead line all trees cutting completed.
2019-08-10 | 5:42 | 18:22 | 12:40 | 0 | 0 | 0 | 5644 | 6143 | 5748 | 11950 | 29485 | 29200 | 285 | 0.976% | 200 | 485 | 144656 | 3142258 | 2.8654 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 16.85% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:42 | 18:22 | 12:40 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Routine Physical Inspection of LT panel & 15 nos Earthpit checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. Today new 3 mW plant, inv-5 replaceing complet,now its running. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. ICR-2, 20 nos table grass cutting completed manually.2nd shift ICR-1 transformer LT side soil digging work done.
2019-08-11 | 05:44 | 18:15 | 12:31 | 0 | 0 | 0 | 4983 | 5590 | 5153 | 11280 | 27006 | 26800 | 206 | 0.7687% | 100 | 306 | 171662 | 3169264 | 2.6245 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.44% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:44 | 18:15 | 12:31 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Routine Physical Inspection of RTU ,MTU panel & Earthpit(MCR,ICR-1)checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. Today jointer come at site and start ICR -1 transformer LT side cable join. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged.
2019-08-12 | 5:52 | 18:09 | 12:17 | 0 | 0 | 0 | 1773 | 1920 | 1792 | 3780 | 9265 | 9100 | 165 | 1.813% | 200 | 365 | 180927 | 3178529 | 0.90039 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.295% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:52 | 18:09 | 12:17 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Routine Physical Inspection of Weather Station & 14 nos Earthpits checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. Today ICR-1 Transformer LT side cable joining completed. 9.new 3 mw plant ACCB-1,INV-1,2& 3 is down due to LT cable damaged. 10. ICR-2, 30 nos table grass cutting completed manually.
2019-08-13 | 5:52 | 18:06 | 12:14 | 0 | 0 | 0 | 4130 | 4539 | 4279 | 8990 | 21938 | 21800 | 138 | 0.633% | 100 | 238 | 202865 | 3200467 | 2.132 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.54% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:52 | 18:06 | 12:14 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Routine Physical Inspection of Fire detector battery checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 9.New 3 mw plant ACCB-1,INV-1,2& 3 is running. 10. ICR-2, 31 nos table grass cutting completed manually.
2019-08-14 | 5:39 | 18:12 | 12:33 | 0 | 0 | 0 | 5118 | 5565 | 5251 | 11980 | 27914 | 27700 | 214 | 0.7726% | 200 | 414 | 230779 | 3228381 | 2.7127 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 15.95% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:39 | 18:12 | 12:33 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of HT panel, VCB panel (MCR) & EarthpitICR-2)checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 9. ICR-2, 27 nos table grass cutting completed manually.
2019-08-15 | 5:47 | 18:12 | 12:25 | 0 | 0 | 0 | 4576 | 4962 | 4690 | 10420 | 24648 | 24300 | 348 | 1.432% | 200 | 548 | 255427 | 3253029 | 2.3953 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.09% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:47 | 18:12 | 12:25 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of HT panel, VCB panel (ICR-1) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 9.Today MSPL street light cable pending work completed
2019-08-16 | 5:44 | 18:10 | 12:26 | 0 | 0 | 0 | 4629 | 5065 | 4889 | 11050 | 25633 | 25500 | 133 | 0.5216% | 200 | 333 | 281060 | 3278662 | 2.4911 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.65% | 17:25 | 15:45 | 132KV substation trip Grid off due to rain. | 1:40 | 1. ICR-1, INV-1,2&3 | 5:44 | 18:10 | 12:26 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of HT panel, VCB panel (ICR-2) checking completed. 5.Street Lights (1 to 22) checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. Grass cutting machine starter not working. 9. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 10. ICR-2, 18 nos table grass cutting completed manually.2nd shift due to rain grass cutting work stop.
2019-08-17 | 5:44 | 16:57 | 11:13 | 0 | 0 | 0 | 3027 | 3279 | 3124 | 6920 | 16350 | 16200 | 150 | 0.9259% | 100 | 250 | 297410 | 3295012 | 1.5889 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.345% |  |  |  |  | 1. ICR-1, INV-1,2&3 | 5:44 | 16:57 | 11:13 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of Auxiliary Transformer(ICR-1) checking completed. 5.Street Lights (23 to 54) checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. Grass cutting machine starter not working. 9. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 10. ICR-2, 22 nos table grass cutting completed manually.2nd shift due to rain grass cutting work stop.
2019-08-18 | 5:51 | 18:12 | 12:21 | 0 | 0 | 0 | 2348 | 2549 | 2409 | 5260 | 12566 | 12400 | 166 | 1.339% | 200 | 366 | 309976 | 3307578 | 1.2212 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 7.182% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:51 | 18:12 | 12:21 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of Power Transformer & Auxiliary Transformer(ICR-2) checking completed. 5.Street Lights (55 to 66) checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. Grass cutting machine starter not working. 9. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 10.ICR-1,INV-1,SMB-7 burn due to ground fault.
2019-08-19 | 5:45 | 18:11 | 12:26 | 0 | 0 | 0 | 4535 | 4959 | 4734 | 10680 | 24908 | 24700 | 208 | 0.8421% | 100 | 308 | 334884 | 3332486 | 2.4206 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.24% | 15:25 | 15:03 | Grid off due to rain. | 0:22 | 1. ICR-1, INV-1,2&3 | 5:45 | 18:11 | 12:26 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of SCADA & DMS panel checking completed. 5.Street Lights (67 to 88) checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. Grass cutting machine starter not working. 9. ICR-2, 30 nos table grass cutting completed manually. 10. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 11.ICR-1,INV-1,SMB-7 burn due to ground fault.
2019-08-20 | 5:46 | 18:25 | 12:39 | 0 | 0 | 0 | 3778 | 4165 | 3952 | 8610 | 20505 | 20400 | 105 | 0.5147% | 200 | 305 | 355389 | 3352991 | 1.9927 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 11.72% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 | 5:46 | 18:25 | 12:39 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of HT switch yard checking completed. 5.Street Lights (89 to 120) checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 7. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 8. Grass cutting machine starter not working. 9. ICR-2, 31 nos table grass cutting completed manually. 10. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 11.ICR-1,INV-1,SMB-7 burn due to ground fault.
2019-08-21 | 5:48 | 18:10 | 12:22 | 0 | 0 | 0 | 3770 | 5108 | 5097 | 11250 | 25225 | 25000 | 225 | 0.9% | 100 | 325 | 380614 | 3378216 | 2.4514 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.42% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2.ICR-2,INV-1,SMB-7 | 1.05:48 2.11:28 | 1.18:10 2.18:10 | 1.12:22 2.06:42 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4..Routine Physical Inspection of RO plant checking completed. 5.ICR-2,INV-1,2,3 Cleaning work not complet. 6.Street Lights (121 to 149) checking not completed. 7. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 8. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 9. Grass cutting machine starter not working. 10. ICR-2, 18 nos table grass cutting completed manually.aAfter help for Transformer work. 11. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 12.ICR-1,INV-1,SMB-7 burn due to ground fault. 13.Today ICR-1 Transformer installation work done.
2019-08-22 | 5:49 | 18:09 | 12:20 | 0 | 0 | 0 | 3695 | 4690 | 4537 | 10040 | 22962 | 22800 | 162 | 0.7105% | 200 | 362 | 403576 | 3401178 | 2.2315 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.12% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2.ICR-2,INV-1,SMB-7 | 5:49 | 18:09 | 12:20 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8.Today grass cutting not completed manually.due to ICR-1 Transformer work. 9. ICR-1 Transformer LT side cable joining completed,but one cable megger value low. 10.ICR-1,INV-1,SMB-7 burn due to ground fault. 11.Today ICR-1 Transformer Earthpit work & HV side tighting work done.
2019-08-23 | 5:49 | 18:12 | 12:23 | 0 | 0 | 0 | 3433 | 4440 | 4219 | 9090 | 21182 | 21000 | 182 | 0.8667% | 100 | 282 | 424758 | 3422360 | 2.0585 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.11% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2.ICR-2,INV-1,SMB-7 | 5:49 | 18:12 | 12:23 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8.ICR-2 ,15 nos grass cutting completed manually. 9.ICR-1,INV-1,SMB-7 burn due to ground fault. 10.Today ICR-1 Transformer oil filling & LT side box fiting work done.
2019-08-24 | 5:49 | 16:30 | 10:41 | 0 | 0 | 0 | 3471 | 4410 | 4179 | 9190 | 21250 | 21100 | 150 | 0.7109% | 200 | 350 | 446008 | 3443610 | 2.0651 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 12.15% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2.ICR-2,INV-1,SMB-7 | 5:49 | 16:30 | 10:41 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4.Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8.ICR-2 ,17 nos grass cutting completed manually. 9.ICR-1,INV-1,SMB-7 burn due to ground fault. 10.Today ICR-1 Transformer HV & LV cable conation complet,HV side megger ,LV side ratio testing completed.
2019-08-25 | 6:04 | 18:02 | 11:58 | 0 | 0 | 0 | 2793 | 3542 | 3350 | 7210 | 16895 | 16700 | 195 | 1.168% | 200 | 395 | 462903 | 3460505 | 1.6419 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.656% |  |  |  | 0:00 | 1. ICR-1, INV-1,2&3 2.ICR-2,INV-1,SMB-7 | 6:04 | 18:02 | 11:58 | 1. Transformer Oil level fail and smoke observed from common neutral bushing. 2.Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1,SMB-7 burn due to ground fault. 9. Today ICR-1 Transformer after all connection completed,we are charge one time (16:30) with out load ,its running 30 minute.When we are give INV load INV-1.3 AC cable is blust . so we are remove LV 1 cable from transformer. Now we are again charge transformer with LV-1 cable and out load, its running with out any problem, morning we start INV-1.1 and 1.2
2019-08-26 | 5:53 | 18:02 | 12:09 | 795 | 1588 | 0 | 2134 | 2436 | 2325 | 4960 | 14238 | 14000 | 238 | 1.7% | 200 | 438 | 477141 | 3474743 | 1.3837 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 8.138% |  |  |  | 0:00 | 1. ICR-1, INV-1,2 2. ICR-1,INV-3 3. ICR-2,INV-1,SMB-7 4. INV-1.1, SMB-7,3 5. INV-1.2, SMB-5 | 1.05:53 2,4&5. 05:53 3.05:53 | 1.08:02 2,4&5.18:02 3.09:21 | 1.02:09:00 2,4&5.12:09:00 3.03:28:00 | 1.RTM relay & AC protation issue. 2.AC cable side blust. 3.Ground fault. 4&5. SMB Burn and Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1,SMB-7 burn due to ground fault. 9.ICR-2,INV-1,SMB-7 running without string nos 13. 10.ICR-1,INV-1 & 2 running.but after 17:05 off due to Auxiliary Transformer problem,now its off condition. 11. INV-1.1, SMB- 5 is running without string no- 12. INV-1.1, SMB-3 is off condition due to ground fault. 12. ICR-1 ,30 nos table grass cutting completed manually.
2019-08-27 | 5:50 | 18:05 | 12:15 | 214 | 316 | 0 | 3134 | 3471 | 3314 | 7240 | 17689 | 17500 | 189 | 1.08% | 100 | 289 | 494830 | 3492432 | 1.719 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 10.11% |  |  |  | 0:00 | 1. ICR-1, INV-1,2 2.ICR-1,INV-3 3. INV-1.1, SMB-7,3 4. INV-1.2, SMB-5 | 1.05:50 2,3&4.05:50 | 1.13:40 2,3&4.18:15 | 1.07:50:00 2,3&4.12:09:00 | 1.Auxiliary supply issue. 2.AC cable side blust. 3&4. SMB Burn and Ground fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Street Lights (121 to 149) checking not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules fauity. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1,SMB-7 burn due to ground fault. 9. ICR-1,INV-1 & 2 running from 13:40. but aux transformer is isolated condition and Auxiliary supply given from MCR. 10. INV-1.1, SMB- 5 is running without string no- 12. INV-1.1, SMB-3 is off condition due to ground fault. 11. ICR-1 ,20 nos table grass cutting completed manually. 12. ICR-2 silica gel replaced.
2019-08-28 | 5:55 | 18:10 | 12:15 | 1705 | 2294 | 0 | 4051 | 4490 | 4278 | 9310 | 26128 | 25900 | 228 | 0.8803% | 200 | 428 | 520958 | 3518560 | 2.5392 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.93% | 9:15 | 8:57 | Grid fail from SS | 0:18 | 1. ICR-1, INV-3 2. ICR-1, INV-1 3. ICR-1, INV-2 4. INV-1.1, SMB-7,3 5. INV-1.2, SMB-5 6. INV-1.1, SMB-1 7. INV-1.2, SMB-4 8. INV-1.2, Node-3 | 1. 05:55 2. 12:20 3. 13:35 4. 05:55 5. 05:55 6. 12:20 7. 13:35 8. 11:30 | 1. 18:10 2. 12:45 3. 13:50 4. 18:10 5. 18:10 6. 18:10 7. 18:10 8. 18:10 | 1. 12:15 2. 00:25 3. 00:15 4. 12:15 5. 12:15 6. 05:50 7. 04:45 8. 06:40 | 1. AC cable side blust and LV cable issue. 2&3. Due to ground fault. 4. SMB burn and ground fault. 5. SMB burnd. 6&7. due to ground fault. 8. AC protection alarm | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Street Lights (121 to 149) checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. INV-1.1, SMB- 5 is running without string no- 12. INV-1.1, SMB-3 and 1 is off condition due to ground fault. 10. ICR-1 ,31 nos table grass cutting completed manually.
2019-08-29 | 6:01 | 18:05 | 12:04 | 1864 | 2566 | 0 | 3764 | 4160 | 3926 | 8540 | 24820 | 24600 | 220 | 0.8943% | 300 | 520 | 545778 | 3543380 | 2.4121 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.19% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-3 4. INV-1.1, SMB-1 5. INV-1.2, SMB-5 6. INV-1.2, SMB-4 7. INV-1.2, Node-3 | 1. 06:01 2. 06:01 3. 06:01 4. 06:01 5. 06:01 6. 06:01 7. 06:01 | 1. 18:05 2. 18:05 3. 13:20 4. 13:10 5. 18:05 6. 18:05 7. 17:20 | 1. 12:04 2. 12:04 3. 07:19 4. 07:09 5. 12:04 6. 12:04 7. 11:19 | 1. AC cable side blust and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to ground fault. 5. SMB burnd. 6. Due to ground fault. 7. AC protection alarm | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 all inverter cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. INV-1.1, SMB- 5, 3 and 1 is running from today. 10. ICR-1 ,30 nos table grass cutting completed manually. 11. INV-2.1 to INV-2.3 OFC cable chenge then also problem not solved, so now it running with old condition.
2019-08-30 | 5:53 | 18:15 | 12:22 | 2147 | 2547 | 0 | 3714 | 4076 | 3836 | 8070 | 24390 | 24100 | 290 | 1.203% | 200 | 490 | 570168 | 3567770 | 2.3703 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.94% | 8:04 | 7:52 | Grid fail from SS | 0:12 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-5 4. INV-1.2, SMB-4 | 5:53 | 18:15 | 12:22 | 1. AC cable side blust and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 all inverter cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,12 nos table grass cutting completed manually.
2019-08-31 | 6:00 | 16:30 | 10:30 | 2183 | 2575 | 0 | 3875 | 3682 | 3859 | 8190 | 24364 | 24200 | 164 | 0.6777% | 100 | 264 | 594532 | 3592134 | 2.3677 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.93% | 16:23 | 16:00 | Grid fail due to rain | 0:23 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-5 4. INV-1.2, SMB-4 05.MCR outgoing VCB panel. | 1. 07:05 2. 07:05 3. 07:05 4. 07:05 5. 06:00 | 1. 16:30 2. 16:30 3. 16:30 4. 16:30 5. 07:05 | 1 to 4. 09:25 5. 01:05 | 1. AC cable side blust and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to over voltage. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. All LA checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,20 nos table grass cutting completed manually.

## Sheet2 (hidden)
Date | TVM reading | Import | LT panel | Export | Import | Inv Gen | Diff
2017-09-01 | 32274.83 | 99.5909 | 27.6692 | 53535.4 | 148.5 | 53936 | 400.6 | 27.752
2017-09-02 | 32330.4418 | 99.7403 | 27.6981 | 55611.8 | 149.4 | 56033 | 421.2 | 28.972 | 28.972
2017-09-03 | 32382.2428 | 99.8818 | 27.7266 | 51801 | 141.5 | 52137 | 336 | 28.468 | 28.468 | 113.032
2017-09-04 | 32430.2394 | 99.9535 | 27.756 | 47996.6 | 71.7 | 48320 | 323.4 | 29.372 | 29.372
2017-09-05 | 32474.8657 | 100.0947 | 27.7853 | 44626.3 | 141.2 | 44921 | 294.7 | 29.348 | 29.348
2017-09-06 | 32511.5792 | 100.2381 | 27.8148 | 36713.5 | 143.4 | 36881 | 167.5 | 29.512 | 29.512
2017-09-07 | 32550.0621 | 100.3773 | 27.8433 | 38482.9 | 139.2 | 38670 | 187.1 | 28.428 | 28.428
2017-09-08 | 32598.9075 | 100.4556 | 27.8713 | 48845.4 | 78.3 | 49145 | 299.6 | 28.098 | 28.098
2017-09-09 | 32639.05 | 100.6 | 27.898 | 40142.5 | 144.4 | 40444 | 301.5 | 26.65 | 26.65
2017-09-10 | 32684.0905 | 100.7618 | 27.9291 | 45040.5 | 161.8 | 45309 | 268.5 | 31.094 | 31.094
2017-09-11 | 32729.8435 | 100.9143 | 27.9571 | 45753 | 152.5 | 46061 | 308 | 28.026 | 28.026
2017-09-12 | 32767.4 | 101.0654 | 27.9852 | 37556.5 | 151.1 | 37846 | 289.5 | 28.08 | 28.08
2017-09-13 | 32805.6649 | 101.2166 | 28.0141 | 38264.9 | 151.2 | 38432 | 167.1 | 28.85 | 28.85
2017-09-14 | 32831.498 | 101.3699 | 28.0406 | 25833.1 | 153.3 | 25942 | 108.9 | 26.594 | 26.594
2017-09-15 | 32864.8153 | 101.5352 | 28.0701 | 33317.3 | 165.3 | 33477 | 159.7 | 29.43 | 29.43
2017-09-16 | 32904.8773 | 101.6886 | 28.099 | 40062 | 153.4 | 40282 | 220 | 28.94 | 28.94
2017-09-17 | 32937.348 | 101.8541 | 28.126 | 32470.7 | 165.5 | 32666 | 195.3 | 26.99 | 26.99
2017-09-18 | 32967.4684 | 102.0074 | 28.1542 | 30120.4 | 153.3 | 30246 | 125.6 | 28.156 | 28.156
2017-09-19 | 32999.55 | 102.15 | 28.182 | 32081.6 | 142.6 | 32263 | 181.4 | 27.84 | 27.84
2017-09-20 | 33026.8175 | 102.3175 | 28.2112 | 27267.5 | 167.5 | 27329 | 61.5 | 29.18 | 29.18
2017-09-21 | 33053.1673 | 102.4323 | 28.2357 | 26349.8 | 114.8 | 26425 | 75.2 | 24.496 | 24.496
2017-09-22 | 33084.8537 | 102.5945 | 28.2638 | 31686.4 | 162.2 | 31851 | 164.6 | 28.106 | 28.106
2017-09-23 | 33135.1119 | 102.7515 | 28.2927 | 50258.2 | 157 | 50611 | 352.8 | 28.904 | 28.904
2017-09-24
2017-09-25
2017-09-26
2017-09-27
2017-09-28
2017-09-29
2017-09-30

## Sep-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Sep-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3000 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | km/h | (°C) | (°C) | (%) | (%) |  | (%)
2019-09-01 | 5:51 | 16:20 | 10:29 | 1876 | 2486 | 0 | 3602 | 3947 | 3781 | 7410 | 23102 | 22800 | 302 | 1.325% | 200 | 502 | 23102 | 3615236 | 2.2451 | 2.1525 | 2.47 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 13.2% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-2,INV-2,NODE-1 6.ICR-1,INV-1,SMB-6 7.ICR-1,INV-1 | 1.05:51 2.05:51 3.05:51 4.05:51 5. 05:51 6.14:00 7.07:08 | 1.16:20 2. 16:20 3. 16:20 4. 16:20 5. 16:20 6.16:20 7.08:24 | 1 to 5. 10:29:00 6. 02:20 7.01:16 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to unbalance AC voltage 6.Due to communication card burn. 7.DC fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR -1 ,INV-1 , all SMB current & voltage checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn.
2019-09-02 | 5:52 | 17:00 | 11:08 | 1842 | 2756 | 0 | 4038 | 4360 | 4505 | 8310 | 25811 | 25600 | 211 | 0.8242% | 300 | 511 | 48913 | 3641047 | 2.5084 | 2.4007 | 2.77 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.75% | 16:58 | 13:10 | Grid fail due to rain | 3:48 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-2,INV-2,NODE-1 6.ICR-1,INV-1,SMB-6 7.ICR-1,INV-2 | 1.05:51 2.05:51 3.05:51 4.05:51 5. 05:51 6.14:00 7.06:43 | 1.17:00 2. 17:00 3. 17:00 4. 17:00 5. 17:00 6.17:00 7.06:50 | 1 to 5. 11:08:00 6. 03:00:00 7. 00:07:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to unbalance AC voltage 6.Due to communication card burn. 7.DC fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR -1 ,INV-2 , 1 to 4 SMB current & voltage checking completed.due rain all SMBs not completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10.ICR-1 ,10 nos table grass cutting completed manually.
2019-09-03 | 5:53 | 18:00 | 12:07 | 1230 | 1849 | 0 | 2678 | 2910 | 2738 | 4960 | 16365 | 16200 | 165 | 1.019% | 200 | 365 | 65278 | 3657412 | 1.5904 | 1.5645 | 1.6533 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.354% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-2,INV-2,NODE-1 6.ICR-1,INV-1,SMB-6 | 5:53 | 18:00 | 12:07 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to unbalance AC voltage 6.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. . ICR -1 ,INV-3 , all SMBs voltage checking completed 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn.
2019-09-04 | 6:05 | 17:55 | 11:50 | 1263 | 1965 | 0 | 2701 | 3010 | 2852 | 4930 | 16721 | 16500 | 221 | 1.339% | 300 | 521 | 81999 | 3674133 | 1.625 | 1.6174 | 1.6433 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.557% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-2,INV-2,NODE-1 6.ICR-1,INV-1,SMB-6 | 6:05 | 17:55 | 11:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to unbalance AC voltage 6.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. . ICR -2 ,INV-1 , all SMB current & voltage checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10.ICR-1 ,30 nos table grass cutting completed manually. 11.After reconnect AC contactor cable we are start node -1 of ICR-2,INV-2,its running.
2019-09-05 | 6:14 | 17:45 | 11:31 | 715 | 1044 | 0 | 1496 | 1686 | 1638 | 2830 | 9409 | 9100 | 309 | 3.396% | 200 | 509 | 91408 | 3683542 | 0.91438 | 0.90247 | 0.94333 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.378% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-1,INV-1,SMB-6 6.ICR-2,INV-2,NODE-1 7.ICR-2,INV-2 | 1.06:14 2.06:14 3.06:14 4.06:14 5. 06:14 6.08:06 7.08:06 | 1.17:45 2. 17:45 3. 17:45 4. 17:45 5. 17:45 6.17:45 7.08:15 | 1 to 5. 11:31:00 6. 09:39:00 7. 00:09:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. 6.Due to unbalance AC voltage. 7.Due to unbalance AC voltage of node -1. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. . ICR -2 ,INV-2 ,SMBs current & voltage checking not completed due to rain. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10.ICR-1 ,10 nos table grass cutting completed manually.
2019-09-06 | 5:56 | 17:10 | 11:14 | 1155 | 1800 | 0 | 2770 | 2997 | 2918 | 5210 | 16850 | 16600 | 250 | 1.506% | 200 | 450 | 108258 | 3700392 | 1.6375 | 1.5967 | 1.7367 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 9.631% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5.ICR-1,INV-1,SMB-6 6.ICR-2,INV-2,NODE-1 7.ICR-1,INV- 1 & 2 | 1.05:56 2.05:56 3.05:56 4.05:56 5. 05:56 6.05:56 7.05:56 | 1.17:10 2. 17:10 3. 17:10 4. 17:10 5. 17:10 6.17:10 7.08:15 | 1 to 6. 11:14:00 7. 02:19:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. 6.Due to unbalance AC voltage. 7.Transformer off due to oil level trip. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. . ICR -2 ,INV-2 ,SMBs current & voltage checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. ICR-1 ,28 nos table grass cutting completed manually.
2019-09-07 | 6:02 | 18:05 | 12:03 | 1852 | 2842 | 0 | 3985 | 4510 | 4142 | 7350 | 24681 | 24400 | 281 | 1.152% | 300 | 581 | 132939 | 3725073 | 2.3985 | 2.3774 | 2.45 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.11% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2,INV-2,NODE-1 7. ICR-1,INV- 1 & 2 8. ICR-2, INV-2.2 | 1. to 8. 06:02 | 1. to 6. 18:05 7. 07:20 8. 06:36 | 1 to 6. 12:03:00 7. 01:18:00 8. 00:34:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. 6.Due to unbalance AC voltage. 7.Transformer off due to oil level trip. 8. Due to unbalance AC voltage we changed contactor and its not solved. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR -2 ,INV-3 ,all SMBs current & voltage checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. ICR-1 ,20 nos table grass cutting completed manually and 5 nos modules shift from store to SMB-2.3.7. 11. ICR-1 all inverters cleaning completed.
2019-09-08 | 5:49 | 18:10 | 12:21 | 1693 | 2599 | 0 | 4400 | 4793 | 4602 | 8090 | 26177 | 26000 | 177 | 0.6808% | 200 | 377 | 159116 | 3751250 | 2.5439 | 2.4811 | 2.6967 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 14.96% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2,INV-2,NODE-1 7. ICR-1,INV- 1 & 2 | 1. to 7. 05:49 | 1. to 6. 18:10 7. 09:18 | 1 to 6. 12:21:00 7. 03:29:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. 6.Due to unbalance AC voltage. 7.Transformer off due to oil level trip. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 all inverters cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. At ICR-1 transformer PRV inside water found with fungal and dust, now clean it and solved that problem.
2019-09-09 | 5:55 | 17:49 | 11:54 | 2317 | 3565 | 0 | 4943 | 5056 | 5165 | 9230 | 30276 | 29900 | 376 | 1.258% | 300 | 676 | 189392 | 3781526 | 2.9423 | 2.887 | 3.0767 | 0.94928 | 949.28 | 215.72 | 0.12 | 32.47 | 35.3 | 114.6% | 110.1% | 2.5886 | 17.3% | 9:08 | 8:55 | Grid fail | 0:13 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2,INV-2,NODE-1 | 1. to 6. 05:49 | 1. to 5. 17:49 6. 16:47 | 1 to 5. 11:54:00 6. 10:58:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. 6.Due to unbalance AC voltage. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of all UPS, battery, battery charger completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. today we removed all faulty modules from structure. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn.
2019-09-10 | 5:47 | 17:50 | 12:03 | 1691 | 2612 | 0 | 3594 | 3987 | 3717 | 6900 | 22501 | 22300 | 201 | 0.9013% | 200 | 401 | 211893 | 3804027 | 2.1867 | 2.1401 | 2.3 | 8.4514 | 8451.38 | 611.65 | 0.28 | 28.58 | 31.74 | 29.67% | 28.9% | 7.3398 | 12.86% | 9:10 | 9:04 | Grid fail | 0:06 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:47 | 17:50 | 12:03 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of all LT panel checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. we removed all faulty modules from structure and connected all good modules. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. ICR-1,2 and MCR earthpit (15 nos) checking completed. 11. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA.
2019-09-11 | 5:54 | 16:40 | 10:46 | 702 | 1099 | 0 | 1522 | 1666 | 1576 | 2920 | 9485 | 9300 | 185 | 1.989% | 200 | 385 | 221378 | 3813512 | 0.92177 | 0.90055 | 0.97333 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 5.421% | 13:00 | 12:14 | Grid fail due to rain | 0:46 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:54 | 16:40 | 10:46 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of RTU and MTU checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 was down due to Modules faulty. we removed all faulty modules from structure and connected all good modules. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. Earth pit checking not completed due to rain. 11. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 12. ICR-1 16 nos table manually grass cutting completed.
2019-09-12 | 5:55 | 17:45 | 11:50 | 1045 | 1640 | 0 | 2260 | 2370 | 2327 | 4100 | 13742 | 13500 | 242 | 1.793% | 200 | 442 | 235120 | 3827254 | 1.3355 | 1.3226 | 1.3667 | 2.2638 | 2263.84 | 200.68 | 1.15 | 26.9 | 28.12 | 56.24% | 55.56% | 2.4082 | 7.854% | 07:15 07:35 10:44 | 07:03 07:26 10:33 | Grid fail due to rain | 00:12 00:12 00:11 total- 00:35 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2, INV-2, Node-1 | 1 to 5. 05:55 6. 07:55 | 1 to 6.17:45 | 1 to 5. 11:50 6. 09:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5. Due to communication card burn. 6. Due to unbalance AC voltage | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of WMS not checking completed due to observation and O&M support, tomorrow we will finish. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. INV-2.3, SMB-7, String -14 and 15 string was start from today. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 10. Earth pit (15 nos) checking completed. 11. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 12. ICR-1 & 2, 31 nos table manually grass cutting completed.
2019-09-13 | 5:50 | 17:50 | 12:00 | 2539 | 3908 | 0 | 5441 | 5485 | 5605 | 10570 | 33548 | 33300 | 248 | 0.7447% | 200 | 448 | 268668 | 3860802 | 3.2603 | 3.152 | 3.5233 | 6.4084 | 6408.41 | 524.2 | 0.83 | 29.37 | 36.32 | 51.83% | 49.58% | 6.2904 | 19.17% | 17:02 | 17:00 | Grid fail | 0:02 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2, INV-2, Node-1 | 1 to 5. 05:50 6. 05:50, 12:35 7. 12:35 | 1 to 5.17:45 6. 11:04, 17:50 7. 12:41 | 1 to 5. 12:00 6. 10:29 7. 00:06 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5. Due to communication card burn. 6. Due to unbalance AC voltage. 7. Due to node-1 AC voltage unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of WMS and fire detectors battery checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 9. all Earth pit checking completed. 10. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 11. ICR-1 & 2, 30 nos table manually grass cutting completed.
2019-09-14 | 5:50 | 17:26 | 11:36 | 2503 | 3889 | 0 | 5501 | 5591 | 5521 | 10590 | 33595 | 33300 | 295 | 0.8859% | 200 | 495 | 302263 | 3894397 | 3.2648 | 3.1557 | 3.53 | 6.914 | 6914 | 612.8 | 0.41 | 31.07 | 38.88 | 45.93% | 43.48% | 7.3536 | 19.2% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. ICR-2, INV-2, Node-1 | 1 to 5. 05:50 6. 05:50 | 1 to 5.17:26 6.11:35 | 1 to 5. 11:36 6. 05:45 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5. Due to communication card burn. 6. Due to unbalance AC voltage. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel, VCB panel of MCR checking & cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 9. Today start Street Light checking. 10. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 11. ICR-1 , 28 nos table manually grass cutting completed.
2019-09-15 | 5:48 | 17:41 | 11:53 | 2322 | 3577 | 0 | 5192 | 5537 | 5222 | 10030 | 31880 | 31600 | 280 | 0.8861% | 300 | 580 | 334143 | 3926277 | 3.0982 | 2.9973 | 3.3433 | 5.7816 | 5781.64 | 505.57 | 0.17 | 30.31 | 38.8 | 51.57% | 48.84% | 6.0668 | 18.22% | 06:14 06:59 | 06:04 06:49 | Grid fail | 00:10 00:10 total- 00:20 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:48 | 17:41 | 11:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel, VCB panel of ICR-1 checking & cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-1 ,INV-1,SMB-6 off due to communication card burn. 9. Yesterday start Street Light checking,today also continue. 10. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA.
2019-09-16 | 5:55 | 17:15 | 11:20 | 2280 | 3589 | 0 | 4731 | 5055 | 3984 | 9490 | 29129 | 28800 | 329 | 1.142% | 200 | 529 | 363272 | 3955406 | 2.8308 | 2.694 | 3.1633 | 5.643 | 5643.02 | 511.19 | 0.31 | 31.48 | 41.23 | 48.86% | 45.82% | 6.1343 | 16.65% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. INV-1.1, SMB-6 | 5:55 | 17:15 | 11:20 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of HT panel, VCB panel of ICR-2 and ICOG-2 checking & cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 1 to 22 Street Light checking completed. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 30 nos table manually grass cutting completed.
2019-09-17 | 5:50 | 17:30 | 11:40 | 1573 | 2451 | 0 | 3347 | 3544 | 3286 | 6380 | 20581 | 20400 | 181 | 0.8873% | 200 | 381 | 383853 | 3975987 | 2.0001 | 1.948 | 2.1267 | 3.8992 | 3899.15 | 337.2 | 0.18 | 29.6 | 35.8 | 50.84% | 48.73% | 4.0464 | 11.76% | 1. 13:41 2. 14:38 | 1. 13:31 2. 14:18 | Grid fail | 0:30 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:50 | 17:30 | 11:40 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of Power Transfermer (ICR-1) tightness checking & cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 23 to 54 Street Light checking completed. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 30 nos table manually grass cutting completed. 11. Today Oil leakage from power transformer of ICR-1 HT side. After tightness, oil leakage has been stopped. 12. ICR-1,INV-1,node-2 side one AC fuse has been changed from INV-1.3,node-2.
2019-09-18 | 5:45 | 17:42 | 11:57 | 1150 | 1762 | 0 | 2427 | 2057 | 2550 | 4730 | 14676 | 14400 | 276 | 1.917% | 200 | 476 | 398529 | 3990663 | 1.4262 | 1.3643 | 1.5767 | 2.8127 | 2812.73 | 233.09 | 0.13 | 27.41 | 29.83 | 51.2% | 50.25% | 2.7971 | 8.388% | 10:37 | 10:04 | Grid fail | 0:33 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:45 | 17:42 | 11:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of Power Transfermer (ICR-2) tightness checking & cleaning not completed due to rain. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 55 to 66 Street Light checking not completed due to rain. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 15 nos table manually grass cutting completed. 11. Today Oil leakage from power transformer of ICR-1 HT side. After tightness, oil leakage has been stopped. 12. ICR-1,INV-1,node-2 side one AC fuse has been changed from INV-1.3,node-2.
2019-09-19 | 5:55 | 17:41 | 11:46 | 1682 | 2581 | 0 | 3457 | 2987 | 3615 | 6530 | 20852 | 20600 | 252 | 1.223% | 200 | 452 | 419381 | 4011515 | 2.0264 | 1.9646 | 2.1767 | 4.0572 | 4057.16 | 352.02 | 0.38 | 28.56 | 33.6 | 48.92% | 47.31% | 4.2242 | 11.92% | 1. 06:47 2. 15:00 | 1. 06:42 2. 14:55 | Grid Fail | 0:10 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 | 1 to 5. 05:55 6. 07:30 | 1 to 6. 17:41 | 1 to 5. 11:46 6. 10:11 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. ACV Unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of SCADA & DMS Panel tightness checking & cleaning have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 67 to 88 Street Light checking not completed due to rain. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 26 nos table manually grass cutting completed. 11. 1.5 MVA Transformer & Auxilary Transformer(75KVA)'s silicagel has been changed.
2019-09-20 | 5:47 | 17:25 | 11:38 | 1920 | 2882 | 0 | 3948 | 3325 | 4123 | 7080 | 23278 | 23100 | 178 | 0.7706% | 200 | 378 | 442659 | 4034793 | 2.2622 | 2.2219 | 2.36 | 4.5868 | 4586.75 | 398.45 | 0.17 | 28.89 | 36.07 | 48.8% | 46.73% | 4.7814 | 13.3% | 1. 09:48 2. 13:44 | 1. 09:35 2. 13:36 | Grid Fail | 0:21 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 7. INV 2.2 8. INV 2.2, SMB-1 | 1 to 6. 05:47 7. 10:20, 10:49 8. 11:20 | 1 to 6. 17:25 7. 10:42, 11:20 8. 17:25 | 1 to 6. 11:38 7. 00:22, 00:31 Total 00:53 8. 06:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. ACV Unbalance. 7. DC Fail 8. Ground Fault | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of Switchyard checking & cleaning have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 89 to 120 Street Light checking not completed due to rain. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 30 nos table manually grass cutting completed. 11. Pending work ICR-2 Power Transformer & Auxilary Transformer checking have completed.
2019-09-21 | 5:49 | 17:30 | 11:41 | 1678 | 2581 | 0 | 3365 | 3354 | 3568 | 6170 | 20716 | 20500 | 216 | 1.054% | 200 | 416 | 463375 | 4055509 | 2.0132 | 1.9953 | 2.0567 | 5.3119 | 5311.91 | 436.69 | 0.26 | 29.96 | 37.19 | 39.46% | 37.61% | 5.2403 | 11.84% | 1. 08:20 2. 09:12 3. 16:30 | 1. 07:30 2. 09:06 3. 14:24 | Grid Fail | 3:02 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 | 5:49 | 17:30 | 11:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. ACV Unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of RO plant checking & cleaning have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. 121 to 149 Street Light checking completed. 9. WMS not working properly with SCADA. we received data every 3min which is need to update every 1 min in SCADA. 10. ICR-2 , 20 nos table manually grass cutting completed. 11. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power.
2019-09-22 | 5:56 | 17:44 | 11:48 | 2177 | 3356 | 0 | 4605 | 4960 | 4703 | 8300 | 28101 | 27800 | 301 | 1.083% | 300 | 601 | 491476 | 4083610 | 2.7309 | 2.7162 | 2.7667 | 5.3114 | 5311.36 | 449.03 | 0.2185 | 29.91 | 37.64 | 51.54% | 49.04% | 5.3884 | 16.06% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 7. INV-2.1, Node-4 8. INV-2.1 | 1 to 6. 05:56 7. 08:00 8. 07:55 | 1 to 8. 17:44 | 1 to 6. 11:48 7. 09:44 8. 00:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. VAC Unbalance. 7. VAC Unbalance. 8. INV trip due to node-4 VAC alarm. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of ICR-2 all Inverters checking & cleaning have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. Physically inspection of LA. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power.
2019-09-23 | 5:53 | 17:33 | 11:40 | 2051 | 3192 | 0 | 4623 | 4590 | 4618 | 8130 | 27204 | 26900 | 304 | 1.13% | 200 | 504 | 518680 | 4110814 | 2.6437 | 2.6165 | 2.71 | 5.3197 | 5319.71 | 459.34 | 0.3 | 29.91 | 37.07 | 49.33% | 47.05% | 5.5121 | 15.55% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 | 5:53 | 1 to 5. 17:33 6. 09:44 | 1 to 5. 11:40 6. 03:51 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. VAC Unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection of ICR-1 all Inverters checking & cleaning have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, 30 nos table manually grass cutting completed. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power.
2019-09-24 | 6:09 | 17:37 | 11:28 | 1196 | 1850 | 0 | 2658 | 1632 | 2611 | 4720 | 14667 | 14500 | 167 | 1.152% | 200 | 367 | 533347 | 4125481 | 1.4254 | 1.3645 | 1.5733 | 2.5586 | 2558.62 | 252.64 | 0.41 | 28.38 | 32.03 | 49.2% | 47.87% | 3.0317 | 8.383% | 6:52 | 6:43 | Grid Fail | 0:09 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 7. ICR-1, INV-2 | 1 to 5. 06:09 6. 07:48 7. 13:00 | 1 to 5. 17:37 6. 13:00 7. 17:37 | 1 to 5. 11:28 6. 05:12 7. 04:37 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. VAC Unbalance. 7. INV trip with blank display, display not working. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection and checking store and cleaning completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, 28 nos table manually grass cutting completed. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. 10. INV-2.2 was trip and display also not working so we didnt found any alarm. we are replaced one OFC PCB card and dispaly from INV1.3 (which was off condition), then also p[roblem not solved.
2019-09-25 | 6:32 | 17:37 | 11:05 | 1327 | 2062 | 0 | 2780 | 3121 | 2510 | 4960 | 16760 | 16500 | 260 | 1.576% | 200 | 460 | 550107 | 4142241 | 1.6288 | 1.6187 | 1.6533 | 3.0128 | 3012.75 | 278.4 | 0.33 | 26.95 | 30.52 | 52.79% | 51.67% | 3.3408 | 9.579% | 10:34 | 10:31 | Grid Fail | 0:03 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 6. INV-2.2, Node-1 | 6:32 | 17:37 | 11:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. VAC Unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physically inspection and checking store and cleaning completed & 1.2 MW site Transformer silica gel changeing completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, 20 nos table manually grass cutting completed,due to rain work stop. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. 10. INV-2.2 display is working after firmaware updateing.
2019-09-26 | 6:09 | 17:31 | 11:22 | 883 | 1378 | 0 | 1357 | 1908 | 1315 | 3400 | 10241 | 10000 | 241 | 2.41% | 200 | 441 | 560348 | 4152482 | 0.99524 | 0.93841 | 1.1333 | 1.8799 | 1879.86 | 176.03 | 0.1 | 26.91 | 25.5 | 49.74% | 49.64% | 2.1124 | 5.853% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. INV-1.1, SMB-6 6. INV-2.2, Node-1 7. ICR-2, INV-2 8. ICR-2, INV-1 9. ICR-2, INV-3 10. INV-2.1, Node-4 11. INV-2.3, Node-2 | 1 to 5. 06:09 6. 09:23 7. 09:13 8. 14:35 9. 14:35 10. 14:55 11. 14:50 | 1 to 5. 17:31 6. 17:31 7. 09:23 8. 14:55 9. 14:50 10. 17:31 11. 17:31 | 1 to 5. 11:22 6. 08:08 7. 00:10 8. 00:20 9. 00:15 10. 02:36 11. 02:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. 6. VAC Unbalance. 7. VAC Unbalance. 8. VAC Unbalance. 9. VAC Unbalance. 10. VAC Unbalance. 11. VAC Unbalance. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Doe to rain all pending work stop. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, 27 nos table manually grass cutting completed,due to rain work stop. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. 10. INV-2.2 display is working after firmaware updateing. 11. From morning site incoming voltage was 35 kV from substation site.
2019-09-27 | 5:56 | 17:30 | 11:34 | 1903 | 2866 | 0 | 4231 | 4594 | 4296 | 6780 | 24670 | 24400 | 270 | 1.107% | 200 | 470 | 585018 | 4177152 | 2.3975 | 2.454 | 2.26 | 5.969 | 5968.98 | 531.74 | 0.14 | 27.9 | 34.86 | 38.98% | 37.5% | 6.3809 | 14.1% | 17:30 | 17:20 | Grid Fail | 0:10 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:56 | 17:30 | 11:34 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Due to rain water coming inside of cable trench, today we are removed water from MCR and ICR-2. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, SMB area water was removed and thats why stop grass cutting. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. today service engineer come at site and told main power bord have some problem and it need to replace and he take 2 days for that replacement. 10. INV-2.2 display is working after firmaware updateing. 11. From morning site incoming voltage was 34 kV upto plant down. 12. M seal puting completed at MCR roof all leakage point. 13. New plant LT Panel-2, UPS connection was wrong (Input and output connection reverse), today we do correct, and UPS connection share to outgoing panel temporary basic.
2019-09-28 | 5:54 | 16:58 | 11:04 | 2270 | 3519 | 0 | 5041 | 5443 | 5127 | 8080 | 29480 | 29200 | 280 | 0.9589% | 200 | 480 | 614498 | 4206632 | 2.8649 | 2.9355 | 2.6933 | 5.685 | 5684.99 | 519.61 | 0.15 | 28.86 | 37.07 | 49.82% | 47.51% | 6.2353 | 16.85% |  |  |  | #VALUE! | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 5:54 | 16:58 | 11:04 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. Due to communication card burn 5. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Due to rain water coming inside of cable trench, today we are removed water from ICR-2. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-2, SMB area water was removed and thats why stop grass cutting. 9. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take 2 days for that replacement. 10. INV-2.2 display is working after firmaware updateing. 11. From morning site incoming voltage was 33 to 34 kV upto plant down.
2019-09-29 | 6:10 | 16:54 | 10:44 | 1662 | 2540 | 0 | 3489 | 3816 | 3645 | 6140 | 21292 | 21000 | 292 | 1.39% | 200 | 492 | 635790 | 4227924 | 2.0692 | 2.0785 | 2.0467 | 7.2528 | 7252.81 | 655.62 | 0.136 | 28 | 32.615 | 29.4% | 28.54% | 7.8674 | 12.17% | 10:05 | 10:00 | Grid Fail | 0:05 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 6:10 | 16:54 | 10:44 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Due to rain water coming inside of cable trench, today we are removed water from ICR-2. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take 2 days for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. Today sometimes weather station is not communacting properly with SCADA.
2019-09-30 | 6:09 | 17:50 | 11:41 | 1434 | 2231 | 0 | 3194 | 3414 | 3256 | 5210 | 18739 | 18500 | 239 | 1.292% | 200 | 439 | 654529 | 4246663 | 1.8211 | 1.8558 | 1.7367 | 6.9912 | 6991.17 | 616.54 | 0.29 | 26.25 | 29.82 | 25.28% | 24.81% | 7.3985 | 10.71% | 17:50 | 17:33 | Grid Fail | 0:17 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 6:09 | 17:50 | 11:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Due to rain water coming inside of cable trench, today we are removed water from ICR-2. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. Today sometimes weather station is not communacting properly with SCADA. 11. 3 MW new plant (plot-5) grass cutting start.

## Oct-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Oct-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3000 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | km/h | (°C) | (°C) | (%) | (%) |  | (%)
2019-10-01 | 6:00 | 17:08 | 11:08 | 1891 | 3182 | 0 | 4339 | 4888 | 4778 | 7790 | 26868 | 26600 | 268 | 1.008% | 200 | 468 | 26868 | 4273531 | 2.6111 | 2.617 | 2.5967 | 9.5614 | 9561.38 | 849.33 | 0.1 | 28.75 | 36.78 | 38.98% | 37.21% | 10.192 | 15.36% | 07:44 13:53 | 07:38 13:52 | Grid off | 00:06 00:01 total- 00:07 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. ICR-1,INV-1,SMB-6 | 6:00 | 17:08 | 11:08 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to ground fault. 4. SMB burnd. 5.Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-1 all modules and SMB's, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. weather station is not communacting properly with SCADA. 11. 3 MW new plant (plot-5 cmpleted, plot -4 start) grass cutting start. 12. ICR-1 ,9 nos table grass cutting completed manually.
2019-10-02 | 5:55 | 17:04 | 11:09 | 2230 | 3576 | 0 | 4821 | 5409 | 5263 | 9200 | 30499 | 30200 | 299 | 0.9901% | 200 | 499 | 57367 | 4304030 | 2.9639 | 2.9217 | 3.0667 | 5.558 | 5558.01 | 501.35 | 0.14 | 29.31 | 37.77 | 74.84% | 71.17% | 6.0162 | 17.43% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV-1.2, SMB-4 | 1 to 4. 05:55 5. 05:55 | 1 to 4. 17:04 5. 13:58 | 1 to 4. 11:09 5. 08:03 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burnd. 5. Due to ground fault (string 8 and 10 off due to comm card senser burnd both place, String removed from SMB side and Modules side both.) | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-2 all modules and SMB's, string Current and Voc checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 cmpleted, plot -4 start) grass cutting start.
2019-10-03 | 5:51 | 17:32 | 11:41 | 2521 | 4505 | 0 | 5554 | 6196 | 6067 | 11850 | 36693 | 36600 | 93 | 0.2541% | 300 | 393 | 94060 | 4340723 | 3.5659 | 3.4078 | 3.95 | 6.5 | 6497.37 | 557.463 | 0.11 | 30.185 | 41 | 77.28% | 72.53% | 6.6896 | 20.97% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:51 | 17:32 | 11:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 INV-3 all modules and SMB's, string Voc were checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 completed, plot -4 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 13. ICR-1, 30nos grass cutting have completed manually.
2019-10-04 | 5:54 | 17:35 | 11:41 | 2285 | 4392 | 0 | 4977 | 5548 | 5523 | 10760 | 33485 | 33200 | 285 | 0.8584% | 200 | 485 | 127545 | 4374208 | 3.2541 | 3.1173 | 3.5867 | 5.95 | 5955.64 | 515.38 | 0.16 | 30.17 | 38.95 | 76.28% | 72.2% | 6.1846 | 19.14% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:54 | 17:35 | 11:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-1 all modules and SMB's, string Voc were checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 & 4 completed, plot -3 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 12. ICR-1, 26 nos grass cutting have completed manually. 13. Due to AC magnetic fault,INV 2.1 NODE-2 was tripping again started automatically. Problem had solved afters discussion with anil (ingeteam).
2019-10-05 | 5:53 | 17:08 | 11:15 | 2146 | 4115 | 0 | 4799 | 4706 | 5197 | 10210 | 31173 | 30800 | 373 | 1.211% | 200 | 573 | 158718 | 4405381 | 3.0294 | 2.8756 | 3.4033 | 5.802 | 5802.96 | 524.05 | 0.075 | 29.86 | 39.05 | 72.53% | 68.62% | 6.2886 | 17.82% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:53 | 17:08 | 11:15 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-2 all modules and SMB's, string Voc were checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 & 4 completed, plot -3 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 12. ICR-1, 30 nos grass cutting have completed manually.
2019-10-06 | 5:54 | 17:06 | 11:12 | 2477 | 4723 | 0 | 5265 | 5033 | 5741 | 12410 | 35649 | 35400 | 249 | 0.7034% | 300 | 549 | 194367 | 4441030 | 3.4644 | 3.1878 | 4.1367 | 6.3673 | 6367.27 | 572.96 | 0.03 | 30.32 | 40.46 | 76.2% | 71.68% | 6.8755 | 20.38% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:54 | 17:06 | 11:12 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 INV-3 all modules and SMB's, string Voc were checking work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 & 4 completed, plot -3 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases.
2019-10-07 | 5:54 | 15:24 | 9:30 | 2133 | 4058 | 0 | 4420 | 4786 | 5239 | 10150 | 30786 | 30500 | 286 | 0.9377% | 200 | 486 | 225153 | 4471816 | 2.9918 | 2.8307 | 3.3833 | 9.1284 | 9128.42 | 945.68 | 0.11 | 29.24 | 40.351 | 47.01% | 44.24% | 11.3482 | 17.6% | 15:24 | 13:58 | Grid off | 1:26 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:54 | 15:24 | 9:30 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-1 all inverters cleaning work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 & 4 completed, plot -3 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 12. Due to fault in incomer at garbham substation, grid incoming is not available. After talking to samaya & substation engg, we isolate our outgoing VCB as well as switchyard VCB. 13. Radiation graph in weather station is not working well. 14. ICR-1, 20 nos grass cutting have completed manually.
2019-10-08 | 5:54 | 17:24 | 11:30 | 334 | 637 | 0 | 669 | 664 | 752 | 1710 | 4766 | 4700 | 66 | 1.404% | 0 | 66 | 229919 | 4476582 | 0.46317 | 0.4192 | 0.57 | 0.83054 | 830.54 | 234 | 0.12 | 28.38 | 31.19 | 24.29% | 23.72% | 2.808 | 2.724% | 13:52 | 5:54 | Grid off | 7:58 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:54 | 17:24 | 11:30 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. ICR-2 all inverters cleaning work completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant (plot-5 & 4 completed, plot -3 continue) grass cutting. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 12. Radiation graph in weather station is not working well. 13. ICR-1, 20 nos grass cutting have completed manually.
2019-10-09 | 5:53 | 17:07 | 11:14 | 2112 | 3841 | 0 | 3968 | 4214 | 5001 | 10110 | 29246 | 29000 | 246 | 0.8483% | 100 | 346 | 259165 | 4505828 | 2.8422 | 2.625 | 3.37 | 5.3515 | 5351.48 | 477.07 | 0.00153 | 29.056 | 38.07 | 53.03% | 50.37% | 5.7248 | 16.72% | 12:09 | 12:07 | Grid off | 0:02 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV 2.1, NODE-2 | 1. to 4. 05:53:00 5. 10:30 | 1. to 4. 17:07:00 5. 11:06 | 1. to 4. 00:09 5. 00:36 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. Showing AC magnectic Fault on respective node. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine checkup & cleaning of all UPS, Battery & Battery charger completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCR UPS was fail, out going supply voltage was zero. we are bypass that connection and now SCADA is running at row power. service engineer come at site and told main power bord have some problem and it need to replace and he take some time for that replacement. 9. From morning site incoming voltage was 33 to 34 kV upto plant down. 10. 3 MW new plant overall grass cutting completed. 11. ICR 2, one AC not working. So ICR-2 room temp increases. 12. ICR-1, 20 nos grass cutting have completed manually. 13. Water evacuation process complete at ICR-2 cable trench. 14. INV 2.1 NODE-2 was showing ac magnetic fault. After talking with CTT & anil(INGETEAM), the problem has been solved.
2019-10-10 | 5:56 | 16:08 | 10:12 | 2061 | 3876 | 0 | 4364 | 4178 | 4921 | 9750 | 29150 | 28900 | 250 | 0.8651% | 300 | 550 | 288315 | 4534978 | 2.8328 | 2.6612 | 3.25 | 5.1252 | 5125.18 | 473.58 | 0.06 | 28.69 | 37.35 | 58.64% | 55.86% | 5.683 | 16.66% | 15:45 | 16:08 | Grid off | 0:23 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:56 | 16:08 | 10:12 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine checkup & cleaning of all LT panels. 5. MCR Earthpit checking completed. 6. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 7. Grass cutting machine starter not working. 8. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 9. Today MCR UPS has repaired by Service Engg. 10. 3 MW new plant overall grass cutting completed. 11. ICR-1, 20 nos grass cutting have completed manually.
2019-10-11 | 6:00 | 16:53 | 10:53 | 2404 | 4658 | 0 | 4913 | 4716 | 5634 | 11470 | 33795 | 33500 | 295 | 0.8806% | 200 | 495 | 322110 | 4568773 | 3.2843 | 3.0624 | 3.8233 | 8.1306 | 8130.58 | 748.286 | 0.021 | 29.187 | 40.31 | 40.33% | 37.96% | 8.9794 | 19.32% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:00 | 16:53 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine checkup & cleaning of RTU & MTU panels have completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. Site visit & overall site survey with Mr. Sujan(VEH) has done today. 9. ICR-1, 31 nos grass cutting have completed manually.
2019-10-12 | 5:53 | 16:27 | 10:34 | 2073 | 4000 | 0 | 4584 | 4331 | 5102 | 10480 | 30570 | 30300 | 270 | 0.8911% | 300 | 570 | 352680 | 4599343 | 2.9708 | 2.7558 | 3.4933 | 7.3579 | 7357.86 | 595.65 | 0.06 | 29.01 | 36.3 | 47.2% | 45.15% | 7.1478 | 17.47% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:53 | 16:27 | 10:34 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine checkup & cleaning of WMS have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. ICR-1, 30 nos grass cutting have completed manually. 9.Earthpit checking today not start due to shortage of manpower.
2019-10-13 | 5:53 | 16:59 | 11:06 | 2282 | 4366 | 0 | 4556 | 4454 | 5429 | 10990 | 32077 | 31800 | 277 | 0.8711% | 200 | 477 | 384757 | 4631420 | 3.1173 | 2.8926 | 3.6633 | 5.7861 | 5786.11 | 526.4 | 0.13 | 29.28 | 39.12 | 53.35% | 50.46% | 6.3168 | 18.33% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV-2.1,NODE-2 | 1 to 4. 05:53 5. 10:38 | 1 to 4. 16:59 5. 10:59 | 1 to 4. 11:06 5. 00:21 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. Showing AC magnectic Fault on respective node. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of Fire Alarm cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Earthpit of ICR-2 checking completed. 9.today we put foam & sealant on MCR roof.
2019-10-14 | 5:55 | 17:21 | 11:26 | 2318 | 4380 | 0 | 4808 | 4517 | 5384 | 11080 | 32487 | 32200 | 287 | 0.8913% | 200 | 487 | 417244 | 4663907 | 3.1571 | 2.9365 | 3.6933 | 5.7091 | 5709.11 | 502.3 | 0.12 | 29.8 | 39 | 54.97% | 52.02% | 6.0276 | 18.57% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV-2.1,NODE-2 | 1 to 4. 05:55 5. 10:30 ,10:48 | 1 to 4. 17:21 5. 10:35,11.04 | 1 to 4. 11:26 5. 00:05, 00:16 total-00:21 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. Showing AC magnectic Fault on respective node. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of HT Panel ,VCB panel of MCR have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Earthpit of ICR-1 checking completed. 9. ICR-1, 30 nos table grass cutting have completed manually.
2019-10-15 | 6:10 | 17:10 | 11:00 | 2242 | 4260 | 0 | 4664 | 4448 | 5211 | 11270 | 32095 | 31800 | 295 | 0.9277% | 300 | 595 | 449339 | 4696002 | 3.119 | 2.8567 | 3.7567 | 5.3792 | 5379.23 | 493.42 | 0.09 | 30.39 | 39.2 | 57.47% | 54.33% | 5.921 | 18.34% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:10 | 17:10 | 11:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of HT Panel ,VCB panel of ICR-1 have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Total Earthpit checking of all SMBs have been completed. 9. ICR-2, 20 nos table grass cutting have completed manually.
2019-10-16 | 5:59 | 17:18 | 11:19 | 1477 | 2856 | 0 | 3313 | 2983 | 3461 | 7430 | 21520 | 21200 | 320 | 1.509% | 200 | 520 | 470859 | 4717522 | 2.0914 | 1.9328 | 2.4767 | 3.3458 | 3345.81 | 304.15 | 0.003 | 28.8 | 33.92 | 60.76% | 58.68% | 3.6498 | 12.3% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:59 | 17:18 | 11:19 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of HT Panel ,VCB panel & ICOG of ICR-2 cleaning & Tightness checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 1 to 22 voltage & tightness checking have been completed. 9. ICR-2, 20 nos table grass cutting have completed manually.
2019-10-17 | 5:57 | 17:23 | 11:26 | 1215 | 2371 | 0 | 2445 | 2332 | 2863 | 6140 | 17366 | 17200 | 166 | 0.9651% | 300 | 466 | 488225 | 4734888 | 1.6877 | 1.5399 | 2.0467 | 2.8709 | 2870.87 | 254.47 | 0.02 | 27.2 | 30.28 | 58.01% | 56.83% | 3.0536 | 9.926% | 13:22 | 12:43 | Due to rain. | 0:39 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:57 | 17:23 | 11:26 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of Power Transformer (ICR-1) checking have not been completed due to rain. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 23 to 54 voltage & tightness checking have not been completed due to rain. 9. ICR-2, 10 nos table grass cutting have completed manually, due to rain work stopped.
2019-10-18 | 5:56 | 17:18 | 11:22 | 1858 | 3662 | 0 | 3684 | 3472 | 4550 | 9870 | 27096 | 26800 | 296 | 1.104% | 200 | 496 | 515321 | 4761984 | 2.6332 | 2.363 | 3.29 | 4.7958 | 4795.76 | 426.08 | 0.02 | 28.36 | 35.64 | 54.37% | 52.15% | 5.113 | 15.49% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV-2.1, NODE-2 | 1 to 4. 05:56 5. 11:10 | 1 to 4. 17:18 5. 11:57 | 1 to 4. 11:22 5. 00:47 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. Showing AC magnectic Fault on respective node. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of Power Transformer (ICR-2) & Auxiliary Transformer checking have been completed,need to change silicagel. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communicetion was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 55 to 66 voltage & tightness checking have been completed. 9. ICR-2, 15 nos table grass cutting have completed manually, due to rain work stopped. 10. Soil Digging for Auxiliary supply cable putting from MCR to ICR-1.
2019-10-19 | 6:08 | 17:22 | 11:14 | 922 | 1791 | 0 | 2060 | 1803 | 2178 | 4530 | 13284 | 13000 | 284 | 2.185% | 300 | 584 | 528605 | 4775268 | 1.291 | 1.2008 | 1.51 | 3.3507 | 3350.67 | 300.01 | 0 | 26.58 | 28.36 | 38.31% | 37.81% | 3.6001 | 7.593% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:08 | 17:22 | 11:14 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of SCADA & DMS panel checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 67 to 88 voltage & tightness checking have not been completed due to rain. 9. ICR-2, 20 nos table grass cutting have completed manually, due to rain work stopped.
2019-10-20 | 7:15 | 17:17 | 10:02 | 1653 | 3104 | 0 | 3663 | 3266 | 3754 | 8190 | 23630 | 23400 | 230 | 0.9829% | 300 | 530 | 552235 | 4798898 | 2.2964 | 2.118 | 2.73 | 3.9774 | 3977.36 | 403.67 | 0.006 | 28.38 | 35.15 | 56.7% | 54.49% | 4.844 | 13.51% | 9:26 | 9:09 | Grid off | 0:17 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 7:15 | 17:17 | 10:02 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of HT switchyard checking have been completed. Most of earthpits have rusted. HT switchyard structure have heavy rust. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 89 to 120 voltage & tightness checking have been completed. 9. MCR auxilary trafo silicagel has been changed.
2019-10-21 | 5:57 | 17:17 | 11:20 | 2168 | 4091 | 0 | 4652 | 4117 | 5041 | 11040 | 31109 | 30800 | 309 | 1.003% | 200 | 509 | 583344 | 4830007 | 3.0232 | 2.7529 | 3.68 | 5.2874 | 5287.4 | 469.52 | 0.05 | 29.84 | 38.23 | 56.81% | 53.93% | 5.6342 | 17.78% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:57 | 17:17 | 11:20 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of RO plant cleaning & checking completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.Street Light of 121 to 149 voltage & tightness checking have been completed. 9.ICR-1, All INVs Cleaning have been completed. 10.ICR-2 ,20 nos table Grass Cutting have been completed manually. 11. Today one cable stated comimg Vizianagaram site from Palamakulla site.
2019-10-22 | 5:55 | 17:10 | 11:15 | 486 | 958 | 0 | 1111 | 1007 | 1160 | 2430 | 7152 | 7000 | 152 | 2.171% | 200 | 352 | 590496 | 4837159 | 0.69504 | 0.64774 | 0.81 | 0.84801 | 848.01 | 75.83 | 0 | 26.53 | 25.52 | 81.47% | 81.31% | 0.90996 | 4.088% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:55 | 17:10 | 11:15 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of all LA checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. Pending work Street Light of 23 to 54 voltage & tightness checking have been completed. 9.ICR-2, All INVs Cleaning have been completed. 10.ICR-2 ,24 nos table Grass Cutting have been completed manually.
2019-10-23 | 7:36 | 16:55 | 9:19 | 419 | 804 | 0 | 929 | 849 | 982 | 1990 | 5973 | 5700 | 273 | 4.789% | 300 | 573 | 596469 | 4843132 | 0.58047 | 0.54636 | 0.66333 | 0.76258 | 762.58 | 84.78 | 0 | 24.44 | 23.731 | 73.49% | 73.85% | 1.0174 | 3.414% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 7:36 | 16:55 | 9:19 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Routine Inspection of POWER TRANSFORMER (ICR-1) checking have not been completed due to contineous rain at site. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8.ICR-2 ,09 nos table Grass Cutting have been completed manually due to rain morning shift work stopped. 9. Water Evacuation process is going on at cable trench. (ICR-2,MCR,ICR-1)
2019-10-24 | 11:20 | 17:27 | 6:07 | 690 | 1301 | 0 | 1444 | 1348 | 1625 | 3470 | 9878 | 9800 | 78 | 0.7959% | 0 | 78 | 606347 | 4853010 | 0.95996 | 0.87901 | 1.1567 | 3.6079 | 3607.88 | 321.82 | 0.015 | 29.85 | 27.37 | 48.77% | 48.32% | 3.8618 | 5.646% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. ICR-1, ICR-2 | 1. to 4. 11:20 5. 08:01:00 | 1. to 4. 17:27 5. 11:20:00 | 1. to 4. 6:07 5. 3:19 Total 09:26 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. All incomers are off due to water inside the cable trench. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7.ICR-2 10 nos table Grass Cutting have been completed manually due to water drainage work morning shift work stopped. 8. Water Evacuation process is going on at cable trench. (ICR-2,MCR,ICR-1)
2019-10-25 | 6:08 | 17:25 | 11:17 | 1849 | 3440 | 0 | 3708 | 3703 | 4204 | 9100 | 26004 | 25800 | 204 | 0.7907% | 300 | 504 | 632351 | 4879014 | 2.5271 | 2.3188 | 3.0333 | 4.3838 | 4383.83 | 394.02 | 0.001 | 29.47 | 36.09 | 56.84% | 54.42% | 4.7282 | 14.86% | 17:02 | 16:52 | Grid off | 0:10 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:08 | 17:25 | 11:17 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7.ICR-2, 25 nos table Grass Cutting have been completed manually. 8.Pending work Routine Inspection of Power Transformer(ICR-1) & Auxiliary Transformer (Auxiliary Transformer not working, ICR-1 Auxiliary Supply givan form MCR) checking completed.
2019-10-26 | 5:59 | 16:54 | 10:55 | 1765 | 3393 | 0 | 3865 | 3554 | 3940 | 8320 | 24837 | 24500 | 337 | 1.376% | 200 | 537 | 657188 | 4903851 | 2.4137 | 2.2657 | 2.7733 | 4.3181 | 4318.09 | 401.54 | 0 | 28.694 | 36.2 | 55.06% | 52.7% | 4.8185 | 14.2% | 8:40 | 8:30 | Grid off | 0:10 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 5. INV 1.1, NODE-3 | 1. to 4.05:59 5. 6:18 | 1. to 4. 16:54 5. 8:07 | 1. to 4. 10:55 5. 1:49 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. AC Fuse failure in inverter. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7.ICR-2, 25 nos table Grass Cutting have been completed manually. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode).
2019-10-27 | 5:57 | 17:11 | 11:14 | 2128 | 3988 | 0 | 4465 | 4357 | 5058 | 10170 | 30166 | 29900 | 266 | 0.8896% | 200 | 466 | 687354 | 4934017 | 2.9316 | 2.7429 | 3.39 | 5.2527 | 5252.67 | 470.71 | 0 | 29.654 | 38.554 | 55.44% | 52.56% | 5.6485 | 17.24% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 5:57 | 17:11 | 11:14 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. INV 15 & INV 28 (3mw plant) are in off position due to AC voltage fault. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode).
2019-10-28 | 6:00 | 17:03 | 11:03 | 2013 | 3754 | 0 | 4384 | 3998 | 4448 | 9210 | 27807 | 27600 | 207 | 0.75% | 300 | 507 | 715161 | 4961824 | 2.7023 | 2.551 | 3.07 | 4.7903 | 4790.27 | 437.49 | 0.113 | 29.877 | 37.48 | 55.9% | 53.22% | 5.2499 | 15.89% | 6:29 | 6:22 | Grid off | 0:07 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:00 | 17:03 | 11:03 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground faild. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28,29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 9. ICR-2, 25 nos table Grass Cutting have been completed manually.
2019-10-29 | 6:05 | 17:10 | 11:05 | 1947 | 3769 | 0 | 4433 | 3928 | 4294 | 8690 | 27061 | 26800 | 261 | 0.9739% | 200 | 461 | 742222 | 4988885 | 2.6298 | 2.52 | 2.8967 | 4.7338 | 4733.76 | 426.5 | 0 | 29.65 | 37.42 | 55.63% | 52.98% | 5.118 | 15.47% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:05 | 17:10 | 11:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28,29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 9. ICR-2, 30 nos table Grass Cutting have been completed manually.
2019-10-30 | 6:03 | 17:02 | 10:59 | 1632 | 3201 | 0 | 3652 | 3271 | 3692 | 7260 | 22708 | 22400 | 308 | 1.375% | 300 | 608 | 764930 | 5011593 | 2.2068 | 2.1191 | 2.42 | 3.7978 | 3797.76 | 347.68 | 0 | 29.33 | 35.48 | 57.79% | 55.46% | 4.1722 | 12.98% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:03 | 17:02 | 10:59 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28,29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 9. ICR-2, 20 nos table Grass Cutting have been completed manually.
2019-10-31 | 6:00 | 17:15 | 11:15 | 1751 | 3380 | 0 | 3969 | 3656 | 4169 | 7940 | 24865 | 24600 | 265 | 1.077% | 200 | 465 | 789795 | 5036458 | 2.4164 | 2.3217 | 2.6467 | 6.1612 | 6161.22 | 547.52 | 0 | 29 | 35.93 | 39.23% | 37.58% | 6.5702 | 14.21% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.1, SMB-6 4. INV-1.2, SMB-5 | 6:00 | 17:15 | 11:15 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. Grass cutting machine starter not working. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 9. ICR-2, 16 nos table Grass Cutting have been completed manually.

## Nov-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Nov-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3000 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | m/s | (°C) | (°C) | (%) | (%) |  | (%)
2019-11-01 | 6:05 | 17:05 | 11:00 | 2292 | 4302 | 0 | 4947 | 4602 | 5206 | 10650 | 31999 | 31700 | 299 | 0.9432% | 300 | 599 | 31999 | 5068457 | 3.1097 | 2.9285 | 3.5465 | 5.4725 | 5472.53 | 500.41 | 0.02 | 31 | 39.93 | 79.74% | 75.17% | 6.0049 | 18.29% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:05 | 17:05 | 11:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-1, INV-1 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 10. ICR-2, 18 nos table & ICR-1, 12 nos table Grass Cutting have been completed manually.
2019-11-02 | 6:02 | 17:09 | 11:07 | 2479 | 4117 | 0 | 4894 | 4531 | 5083 | 10280 | 31384 | 31200 | 184 | 0.5897% | 300 | 484 | 63383 | 5099841 | 3.05 | 2.8949 | 3.4232 | 5.3469 | 5346.89 | 487.02 | 0 | 30 | 38.81 | 79.52% | 75.3% | 5.8442 | 17.94% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:02 | 17:09 | 11:07 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-1, INV-2 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 10.ICR-1, 27 nos table Grass Cutting have been completed manually.
2019-11-03 | 6:00 | 17:07 | 11:07 | 2584 | 4370 | 0 | 5052 | 4687 | 5281 | 10700 | 32674 | 32400 | 274 | 0.8457% | 200 | 474 | 96057 | 5132515 | 3.1753 | 3.0143 | 3.5631 | 5.589 | 5589.03 | 506.63 | 0 | 39.17 | 30.101 | 79.58% | 78.02% | 6.0796 | 18.68% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:00 | 17:07 | 11:07 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-1, INV-3 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode).
2019-11-04 | 6:00 | 17:05 | 11:05 | 2557 | 4150 | 0 | 4645 | 4634 | 4887 | 10790 | 31663 | 31400 | 263 | 0.8376% | 300 | 563 | 127720 | 5164178 | 3.0771 | 2.8632 | 3.5931 | 5.3937 | 5393.7 | 489.55 | 0 | 38.77 | 30 | 80.05% | 78.51% | 5.8746 | 18.1% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:00 | 17:05 | 11:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-2, INV-1 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 10. One module(GCL-320wp) replaced with new one as it was damaged. Location (INV 2.1, SMB 4, St-4, #36) 11.ICR-1, 20 nos table Grass Cutting have been completed manually.
2019-11-05 | 6:09 | 17:09 | 11:00 | 2171 | 3716 | 0 | 4096 | 4200 | 4493 | 9080 | 27756 | 27500 | 256 | 0.9309% | 200 | 456 | 155476 | 5191934 | 2.6974 | 2.5619 | 3.0236 | 4.6268 | 4626.83 | 423.3 | 0 | 30 | 36.54 | 81.77% | 78.15% | 5.0796 | 15.86% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:09 | 17:09 | 11:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-2, INV-2 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 10. 4 nos ports at Communication card(-ve side) of SMB 4 of INV 1.1 has been replaced with spare points. 11.ICR-1, 20 nos table Grass Cutting have been completed manually.
2019-11-06 | 6:01 | 17:08 | 11:07 | 2520 | 4024 | 0 | 4380 | 4943 | 4707 | 9730 | 30304 | 30000 | 304 | 1.013% | 300 | 604 | 185780 | 5222238 | 2.945 | 2.8222 | 3.2401 | 4.9556 | 4955.61 | 447.95 | 0.04 | 29 | 35.51 | 83.48% | 80.11% | 5.3754 | 17.32% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:01 | 17:08 | 11:07 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-2, INV-3 all SMBs voltage and current cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. Grass cutting machine starter not working. 7. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 8. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 9. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 10.ICR-1, 20 nos table Grass Cutting have been completed manually.
2019-11-07 | 6:03 | 17:08 | 11:05 | 2697 | 4310 | 0 | 4698 | 5309 | 5163 | 10550 | 32727 | 32500 | 227 | 0.6985% | 300 | 527 | 218507 | 5254965 | 3.1805 | 3.0421 | 3.5132 | 5.2368 | 5236.79 | 474.51 | 0.01 | 28.26 | 35.04 | 85.36% | 82.07% | 5.6941 | 18.71% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:03 | 17:08 | 11:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-1, INV-1,2,3 cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup(Bypass Mode). 9.ICR-1, 10 nos table Grass Cutting have been completed manually.2nd shift boundary fencing site small trees cutting work .
2019-11-08 | 6:07 | 17:04 | 10:57 | 2047 | 3234 | 0 | 3564 | 4032 | 3890 | 7840 | 24607 | 24400 | 207 | 0.8484% | 200 | 407 | 243114 | 5279572 | 2.3914 | 2.3 | 2.6107 | 4.0723 | 4072.27 | 375.22 | 0 | 28 | 34.06 | 82.15% | 81.21% | 4.5026 | 14.06% | 11:00 | 10:33 | Grid Fail | 0:27 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:07 | 17:04 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of ICR-2, INV-1,2,3 cleaning & cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup (Bypass Mode). 9. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to R.O. plant)
2019-11-09 | 6:06 | 17:10 | 11:04 | 2715 | 4326 | 0 | 4720 | 5383 | 5132 | 10690 | 32966 | 32700 | 266 | 0.8135% | 300 | 566 | 276080 | 5312538 | 3.2037 | 3.0557 | 3.5598 | 5.3396 | 5339.55 | 485.3 | 0.01 | 29.21 | 36.75 | 84.2% | 82.84% | 5.8236 | 18.84% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:06 | 17:10 | 11:04 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of battery,UPS & battery charger cleaning & cheking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup (Bypass Mode). 9. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to R.O. plant)
2019-11-10 | 6:03 | 17:02 | 10:59 | 2942 | 4682 | 0 | 5127 | 5785 | 5577 | 11720 | 35833 | 35600 | 233 | 0.6545% | 300 | 533 | 311913 | 5348371 | 3.4823 | 3.3077 | 3.9028 | 5.9303 | 5930.27 | 543.49 | 0.03 | 30 | 39.19 | 82.34% | 80.76% | 6.5219 | 20.48% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:03 | 17:02 | 10:59 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of LT panels cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. ICR - 2 UPS is not supporting battery bank. Now it is running without backup (Bypass Mode).
2019-11-11 | 6:02 | 17:04 | 11:02 | 2875 | 4592 | 0 | 5072 | 5727 | 5547 | 11480 | 35293 | 34900 | 393 | 1.126% | 300 | 693 | 347206 | 5383664 | 3.4298 | 3.2665 | 3.8228 | 5.8485 | 5848.51 | 534.06 | 0.04 | 29.91 | 38.78 | 82.16% | 80.61% | 6.4087 | 20.17% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:02 | 17:04 | 11:02 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of RTU & MTU panels cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Today UPS Service Engineer visited at site & found 2no battery have some issue in ICR - 2 UPS, Is not supporting battery bank. Now it is running without backup (Bypass Mode). 9.6 nos of Earthpit today checking have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to R.O. plant)
2019-11-12 | 6:04 | 17:03 | 10:59 | 2544 | 4489 | 0 | 4902 | 5537 | 5386 | 11140 | 33998 | 33800 | 198 | 0.5858% | 300 | 498 | 381204 | 5417662 | 3.304 | 3.1355 | 3.7096 | 5.6485 | 5648.49 | 516.93 | 0.08 | 29 | 37.82 | 82.14% | 80.88% | 6.2032 | 19.43% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:04 | 17:03 | 10:59 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of weather monitoring system cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. 6 nos of Earthpit today checking have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to R.O. plant)
2019-11-13 | 6:05 | 17:07 | 11:02 | 2828 | 4514 | 0 | 4855 | 5540 | 5370 | 11110 | 34217 | 33900 | 317 | 0.9351% | 300 | 617 | 415421 | 5451879 | 3.3253 | 3.1697 | 3.6996 | 5.6946 | 5694.57 | 520.2 | 0.05 | 28 | 37.68 | 81.78% | 80.84% | 6.2424 | 19.56% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:05 | 17:07 | 11:02 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of fire alram & fire extinguiser cleaning & checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. 6 nos of Earthpit today checking have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to Konda site)
2019-11-14 | 6:05 | 17:01 | 10:56 | 2704 | 4309 | 0 | 4705 | 5331 | 5138 | 10550 | 32737 | 32500 | 237 | 0.7292% | 300 | 537 | 448158 | 5484616 | 3.1814 | 3.0435 | 3.5132 | 5.3883 | 5388.29 | 497.38 | 0.06 | 27.49 | 36.26 | 82.58% | 79.01% | 5.9686 | 18.71% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:05 | 17:01 | 10:56 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of HT panel of MCR cleaning & tightness checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. 12 nos of Earthpit(MCR,ICR-1,2) today checking have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to Konda site)
2019-11-15 | 6:04 | 17:01 | 10:57 | 2789 | 4447 | 0 | 4865 | 5517 | 5308 | 11020 | 33946 | 33700 | 246 | 0.73% | 200 | 446 | 482104 | 5518562 | 3.2989 | 3.1449 | 3.6697 | 5.6504 | 5650.41 | 521.6 | 0.1 | 27.69 | 37.26 | 81.53% | 77.69% | 6.2592 | 19.4% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:04 | 17:01 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of HT panel of ICR-1cleaning & tightness checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. All Earthpit checking & tightness have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on(from main gate to Konda site)
2019-11-16 | 6:06 | 17:03 | 10:57 | 2760 | 4400 | 0 | 4791 | 5440 | 5228 | 10440 | 33059 | 32800 | 259 | 0.7896% | 300 | 559 | 515163 | 5551621 | 3.2127 | 3.1027 | 3.4765 | 5.5701 | 5570.14 | 519.74 | 0.03 | 28.34 | 38.38 | 79.68% | 75.59% | 6.2369 | 18.9% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:06 | 17:03 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of HT panel of ICR-2 & ICOG-1 cleaning & tightness checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 01to 22 checking & tightness have been completed. 10. Fencing boundary overlapped tree & bushes cutting is going on manually (from main gate to Konda site).
2019-11-17 | 6:10 | 17:02 | 10:52 | 2489 | 3954 | 0 | 4302 | 4921 | 4681 | 9210 | 29557 | 29300 | 257 | 0.8771% | 200 | 457 | 544720 | 5581178 | 2.8724 | 2.7911 | 3.0669 | 5.4341 | 5434.15 | 501.58 | 0.03 | 29 | 38.72 | 74.39% | 70.47% | 6.019 | 16.89% | 8:58 | 7:58 | Grid Fail | 1:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:10 | 17:02 | 10:52 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of power transformer ICR-1 checking have been completed. Oil leakage found on drain valve. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 23 to 54 checking have been completed.
2019-11-18 | 6:07 | 17:01 | 10:54 | 2774 | 4424 | 0 | 4821 | 5474 | 5272 | 10340 | 33105 | 32900 | 205 | 0.6231% | 300 | 505 | 577825 | 5614283 | 3.2172 | 3.1228 | 3.4432 | 5.5158 | 5515.78 | 511.47 | 0.09 | 29 | 38.32 | 81.46% | 77.29% | 6.1376 | 18.92% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:07 | 17:01 | 10:54 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of power transformer ICR-2 checking have not been completed due to some other work. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 55 to 66 checking have been completed.
2019-11-19 | 6:07 | 17:04 | 10:57 | 2338 | 3713 | 0 | 4033 | 4560 | 4469 | 8580 | 27693 | 27400 | 293 | 1.069% | 200 | 493 | 605518 | 5641976 | 2.6913 | 2.6218 | 2.8571 | 4.5911 | 4591.06 | 423.83 | 0.11 | 28 | 35.25 | 81.85% | 78.63% | 5.086 | 15.83% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:07 | 17:04 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of power transformer ICR-2 checking have been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 67 to 88 checking have been completed. 10. SCADA / DMS panel tightness checking & cleaning have been completed.
2019-11-20 | 6:11 | 17:03 | 10:52 | 2129 | 3379 | 0 | 3589 | 4144 | 4042 | 7710 | 24993 | 24800 | 193 | 0.7782% | 300 | 493 | 630511 | 5666969 | 2.4289 | 2.3708 | 2.5674 | 4.111 | 4110.97 | 380.97 | 0.02 | 27 | 34.15 | 82.81% | 79.9% | 4.5716 | 14.28% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:11 | 17:03 | 10:52 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of HT Switch-yard checking has been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 89 to 120 checking have been completed. 10. Today 4 nos of table grass cutting have been completed manually.
2019-11-21 | 6:10 | 17:03 | 10:53 | 2620 | 4176 | 0 | 4523 | 5135 | 4958 | 10390 | 31802 | 31600 | 202 | 0.6392% | 200 | 402 | 662313 | 5698771 | 3.0906 | 2.9372 | 3.4599 | 5.271 | 5270.95 | 488.07 | 0.13 | 27 | 35.81 | 82.13% | 78.72% | 5.8568 | 18.18% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:10 | 17:03 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of R.O. Plant checking has been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today street tights 121 to 149 checking have been completed. 10. Today 4 nos of table grass cutting have been completed manually. 11. Physical inspection of all inverters of ICR-1 checking & cleaning have been completed.
2019-11-22 | 6:11 | 17:02 | 10:51 | 2552 | 4058 | 0 | 4401 | 5052 | 4873 | 10270 | 31206 | 31000 | 206 | 0.6645% | 200 | 406 | 693519 | 5729977 | 3.0327 | 2.8719 | 3.4199 | 5.213 | 5213 | 483.63 | 0.02 | 27 | 36.23 | 81.58% | 78.06% | 5.8036 | 17.84% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:11 | 17:02 | 10:51 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of LA checking has not been completed due to other work. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today INV 32 (new 3mw plant) is showing GRID OVERVOLTAGE (OV) alram. The cable from MCCB to INV (70 mm², 3C) have fault. MCCB terminal showing voltages but that is not reflected on INV end terminal. 10. Today 3 nos of table grass cutting have been completed manually. 11. Physical inspection of all inverters of ICR-2 checking & cleaning have been completed.
2019-11-23 | 6:10 | 17:04 | 10:54 | 1820 | 3652 | 0 | 3988 | 4545 | 4418 | 9300 | 27723 | 27500 | 223 | 0.8109% | 300 | 523 | 721242 | 5757700 | 2.6942 | 2.5272 | 3.0969 | 4.6799 | 4679.94 | 434.6 | 0.01 | 27 | 34.79 | 80.28% | 77.26% | 5.2152 | 15.85% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:10 | 17:04 | 10:54 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of LA checking has not been completed due to other work. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today 3 nos of table grass cutting have been completed manually. 10. Today we have checked the ACCB-7 regarding cable issue.
2019-11-24 | 6:10 | 17:03 | 10:53 | 1884 | 3501 | 0 | 3730 | 4253 | 4175 | 8050 | 25593 | 25300 | 293 | 1.158% | 200 | 493 | 746835 | 5783293 | 2.4872 | 2.4064 | 2.6807 | 4.3533 | 4353.31 | 405.25 | 0.01 | 26 | 33.56 | 79.6% | 76.98% | 4.863 | 14.63% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:10 | 17:03 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of LA checking has not been completed due to other work. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29 & 30(3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. ACCB-7 full checking have been completed today.
2019-11-25 | 6:13 | 17:12 | 10:59 | 2107 | 3967 | 0 | 4289 | 4882 | 4696 | 9080 | 29021 | 28900 | 121 | 0.4187% | 300 | 421 | 775856 | 5812314 | 2.8203 | 2.7354 | 3.0236 | 5.0625 | 5062.47 | 465.06 | 0.08 | 27 | 35.17 | 77.94% | 74.89% | 5.5807 | 16.59% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:13 | 17:12 | 10:59 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. Physical inspection of LA checking has been completed. 5. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. Today 3 nos of table grass cutting have been completed.
2019-11-26 | 6:13 | 17:10 | 10:57 | 2072 | 3938 | 0 | 4257 | 4844 | 4672 | 9040 | 28823 | 28600 | 223 | 0.7797% | 300 | 523 | 804679 | 5841137 | 2.8011 | 2.7137 | 3.0103 | 5.0831 | 5083.1 | 316.26 | 0.08 | 24 | 28.05 | 114.2% | 112.8% | 3.7951 | 16.47% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:13 | 17:10 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. Today 3 nos of table grass cutting have been completed.
2019-11-27 | 6:13 | 17:10 | 10:57 | 1933 | 3665 | 0 | 3958 | 4513 | 4354 | 8570 | 26993 | 26700 | 293 | 1.097% | 200 | 493 | 831672 | 5868130 | 2.6232 | 2.5272 | 2.8538 | 4.6602 | 4660.17 | 427.36 | 0.08 | 27 | 33.82 | 79.13% | 76.45% | 5.1283 | 15.43% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 | 6:13 | 17:10 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. Due to rain All Modules Cleaned. 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. Today 3 nos of table grass cutting have been completed. 9. LT PANEL-1, ACCB-1 feeder is trip. In the otherend the MCCB is in off condition, but tripping happen. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. Today silicagel change has done at 1.25MVA TRAFO (3MW).
2019-11-28 | 6:14 | 17:12 | 10:58 | 1813 | 3412 | 0 | 3605 | 4172 | 4049 | 7030 | 24081 | 23900 | 181 | 0.7573% | 300 | 481 | 855753 | 5892211 | 2.3402 | 2.339 | 2.341 | 4.3843 | 4384.33 | 392.57 | 0.08 | 27 | 33.29 | 76.73% | 74.29% | 4.7108 | 13.76% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LTP-2(1.5MW), ACCB-7 6. LTP-1(1.25MW), ACCB-1 7. LTP-1(1.25MW) | 1. to 6 06:14:00 7. 11:00 | 1. to 6. 17:12:00 7. 13:12 | 1. to 6. 10:58 7. 2:12 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs are burnt. 6. Cable fault 7. For ACCB-1 Testing | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. Today 3 nos of table grass cutting have been completed. 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-11-29 | 6:14 | 17:07 | 10:53 | 2123 | 3992 | 0 | 4238 | 4812 | 4672 | 9350 | 29187 | 28900 | 287 | 0.9931% | 200 | 487 | 884940 | 5921398 | 2.8364 | 2.7211 | 3.1136 | 5.1328 | 5132.82 | 471.98 | 0.07 | 28 | 36.44 | 77.94% | 74.52% | 5.6638 | 16.68% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LTP-2(1.5MW), ACCB-7 6. LTP-1(1.25MW), ACCB-1 | 6:14 | 17:02 | 10:48 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs are burnt. 6. Cable fault | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. Today 3 nos of table grass cutting have been completed. 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. We replaced a 24mtr long street light cable at 3mw plant location.
2019-11-30 | 6:17 | 17:10 | 10:53 | 2038 | 3884 | 0 | 4190 | 4749 | 4532 | 9120 | 28513 | 28300 | 213 | 0.7527% | 200 | 413 | 913453 | 5949911 | 2.7709 | 2.6602 | 3.037 | 5.0428 | 5042.82 | 466.44 | 0.13 | 28 | 36.29 | 77.05% | 73.71% | 5.5973 | 16.3% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LTP-2(1.5MW), ACCB-7 6. LTP-1(1.25MW), ACCB-1 | 6:17 | 17:10 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs are burnt. 6. Cable fault | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. Today 3 nos of table grass cutting have been completed. 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.

## Dec-19
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Dec-2019 | Cumulative (FY 2019-2020) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3003 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | m/s | (°C) | (°C) | (%) | (%) |  | (%)
2019-12-01 | 6:19 | 17:17 | 10:58 | 1437 | 2987 | 0 | 3239 | 3700 | 3574 | 6850 | 21787 | 21600 | 187 | 0.8657% | 300 | 487 | 21787 | 5971698 | 2.1173 | 2.049 | 2.2811 | 3.9543 | 3954.29 | 364.47 | 0.07 | 27 | 32.77 | 74.77% | 72.54% | 4.3736 | 12.45% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 1. to 6. 06:19 7. 11:42 | 17:17 | 1. to 6. 10:58 7. 5:42 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. Today INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-1, INV-1 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-12-02 | 6:21 | 17:13 | 10:52 | 916 | 2027 | 0 | 2215 | 2504 | 2428 | 4540 | 14630 | 14500 | 130 | 0.8966% | 300 | 430 | 36417 | 5986328 | 1.4218 | 1.3841 | 1.5118 | 2.4258 | 2425.84 | 225.89 | 0.09 | 27 | 29.51 | 81.76% | 80.34% | 2.7107 | 8.362% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:21 | 17:13 | 10:52 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-1, INV-2 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-12-03 | 6:19 | 17:14 | 10:55 | 1607 | 3539 | 0 | 3821 | 4338 | 4182 | 8120 | 25607 | 25400 | 207 | 0.815% | 200 | 407 | 62024 | 6011935 | 2.4885 | 2.3988 | 2.704 | 4.6365 | 4636.47 | 419.67 | 0.27 | 27 | 33.92 | 76.67% | 74.05% | 5.036 | 14.64% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:19 | 17:14 | 10:55 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-1, INV-3 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today grass cutting completed from R.O. plant to MCR (ROAD SIDE Only) & Block no 32 to 31 (5 tables) Module cleaning work completed.
2019-12-04 | 6:19 | 17:41 | 11:22 | 1747 | 3883 | 0 | 4024 | 4694 | 4526 | 9040 | 27914 | 27700 | 214 | 0.7726% | 300 | 514 | 89938 | 6039849 | 2.7127 | 2.589 | 3.0103 | 5.0128 | 5012.8 | 437.81 | 0.33 | 26 | 33.62 | 76.94% | 74.4% | 5.2537 | 15.95% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:19 | 17:41 | 11:22 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-2, INV-1 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today Block no 31 to 29 (11 tables) Module cleaning work completed in first shift &one no of table grass cutting completed in second shift.
2019-12-05 | 6:19 | 17:14 | 10:55 | 1739 | 3873 | 0 | 4139 | 4657 | 4525 | 9010 | 27943 | 27700 | 243 | 0.8773% | 200 | 443 | 117881 | 6067792 | 2.7155 | 2.5971 | 3.0003 | 5.1617 | 5161.7 | 474.13 | 0.32 | 25.83 | 33.39 | 74.06% | 71.67% | 5.6896 | 15.97% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:19 | 17:14 | 10:55 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-2, INV-2 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 3 nos grass cutting have been completed manually.
2019-12-06 | 6:20 | 17:12 | 10:52 | 1844 | 4112 | 0 | 4375 | 5014 | 4768 | 9620 | 29733 | 29500 | 233 | 0.7898% | 300 | 533 | 147614 | 6097525 | 2.8895 | 2.759 | 3.2035 | 5.3235 | 5323.47 | 490 | 0.15 | 24.99 | 33.45 | 76.6% | 74.11% | 5.88 | 16.99% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:20 | 17:12 | 10:52 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-2, INV-3 all SMBs voltage and current cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 4 nos grass cutting have been completed manually.
2019-12-07 | 6:08 | 17:13 | 11:05 | 1322 | 2936 | 0 | 3181 | 3576 | 3396 | 6980 | 21391 | 21200 | 191 | 0.9009% | 200 | 391 | 169005 | 6118916 | 2.0788 | 1.9768 | 2.3243 | 5.0952 | 5095.21 | 452.32 | 0.11 | 26.14 | 34.07 | 58.53% | 56.49% | 5.4278 | 12.23% | 13:20 | 11:38 | Gird fail(substation maintance by govt.) | 1:42 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:08 | 17:13 | 11:05 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-1, INV-1,2,3 cleaning & cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 2 nos grass cutting have been completed manually.2nd shift ICR-1 & 2 front side grass cutting.
2019-12-08 | 6:21 | 17:17 | 10:56 | 1094 | 2961 | 0 | 3270 | 3665 | 3533 | 7230 | 21753 | 21500 | 253 | 1.177% | 300 | 553 | 190758 | 6140669 | 2.114 | 1.9922 | 2.4076 | 4.107 | 4107.02 | 372.57 | 0.36 | 26.55 | 32.63 | 73.25% | 71.11% | 4.4708 | 12.43% | 1. 08:05 2. 11:29 | 1. 08:02 2. 11:20 | Grid Fail(Ovre voltage) | 0:12 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 8.ICR-1,INV-1 9.INV-1.1, SMB-3 | 1 to7 .06:21 8. 08:07 9. 08:07 | 1 to7 .17:17 8. 09:09 9. 10:00 | 1 to7. 10:56 8. 01:02 9.01:53 |  | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of ICR-2, INV-1,2,3 cleaning & cheking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-12-09 | 6:20 | 17:17 | 10:57 | 1579 | 3696 | 0 | 3783 | 4450 | 4423 | 8830 | 26761 | 26600 | 161 | 0.6053% | 200 | 361 | 217519 | 6167430 | 2.6007 | 2.4597 | 2.9404 | 4.837 | 4837.01 | 448.68 | 0.51 | 27 | 34.61 | 74.72% | 71.96% | 5.3842 | 15.3% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:20 | 17:17 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of UPSs, Batteries and Battery chargers cleaning & checking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today structure painting work start at Switchyard.
2019-12-10 | 6:21 | 17:14 | 10:53 | 1449 | 3464 | 0 | 3747 | 4249 | 4187 | 8320 | 25416 | 25200 | 216 | 0.8571% | 200 | 416 | 242935 | 6192846 | 2.47 | 2.3451 | 2.7706 | 4.5427 | 4542.66 | 404.7 | 0.22 | 26 | 33.29 | 79.16% | 76.64% | 4.8564 | 14.53% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:21 | 17:14 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of all LT Panels cleaning & checking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today INV 1.2 SMBs Earthpit tightness checking have completed.
2019-12-11 | 6:20 | 17:07 | 10:47 | 1553 | 3722 | 0 | 3892 | 4478 | 4314 | 8800 | 26759 | 26500 | 259 | 0.9774% | 200 | 459 | 269694 | 6219605 | 2.6005 | 2.4635 | 2.9304 | 5.0207 | 5020.74 | 452.03 | 0.42 | 26 | 34.32 | 75.3% | 72.61% | 5.4244 | 15.29% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:20 | 17:17 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of all RTU & MTU Panels cleaning & checking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-12-12 | 6:22 | 16:11 | 9:49 | 1098 | 2594 | 0 | 2735 | 3103 | 3038 | 6150 | 18718 | 18500 | 218 | 1.178% | 300 | 518 | 288412 | 6238323 | 1.819 | 1.724 | 2.048 | 3.5019 | 3501.92 | 344.74 | 0.3 | 25 | 31.24 | 75.87% | 74.05% | 4.1369 | 10.7% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:22 | 16:11 | 9:49 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of weather monitoring system cleaning & checking have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today tree branches cutting have done.
2019-12-13 | 6:23 | 17:17 | 10:54 | 1311 | 3240 | 0 | 3489 | 4034 | 3993 | 7930 | 23997 | 23800 | 197 | 0.8277% | 200 | 397 | 312409 | 6262320 | 2.3321 | 2.204 | 2.6407 | 4.2484 | 4248.42 | 396.15 | 0.24 | 26 | 32.79 | 76.23% | 73.95% | 4.7538 | 13.72% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:23 | 17:17 | 10:54 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of Fire detector & alram cleaning & checking have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 15 nos tables grass cutting were done by outside labour. 13. Today 8 nos tables grass cutting were done by grass cutting machine.
2019-12-14 | 6:21 | 17:14 | 10:53 | 1446 | 3501 | 0 | 3785 | 4264 | 4088 | 8220 | 25304 | 25100 | 204 | 0.8127% | 300 | 504 | 337713 | 6287624 | 2.4591 | 2.3435 | 2.7373 | 4.5915 | 4591.53 | 412.46 | 0.58 | 27 | 34.09 | 77.32% | 74.63% | 4.9495 | 14.46% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:21 | 17:14 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of HT panel(MCR OUTGOING) have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 34 nos tables grass cutting were done by outside labour manually. 13. Today 28 nos tables grass cutting were done by grass cutting machine.
2019-12-15 | 6:23 | 17:14 | 10:51 | 1136 | 3887 | 0 | 4151 | 4715 | 4579 | 9270 | 27738 | 27500 | 238 | 0.8655% | 200 | 438 | 365451 | 6315362 | 2.6956 | 2.5333 | 3.0869 | 5.1914 | 5191.35 | 478.17 | 0.28 | 26 | 34.76 | 73.34% | 70.59% | 5.738 | 15.85% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:23 | 17:14 | 10:51 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of HT panel(iCR-1) have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 54 nos tables grass cutting were done by outside labour manually. 13. Today 19 nos tables grass cutting were done by grass cutting machine. 14. Today 23 nos tables grass cutting were done by TRACTOR machine.
2019-12-16 | 6:25 | 17:14 | 10:49 | 1411 | 3345 | 0 | 3332 | 3830 | 3927 | 7920 | 23765 | 23600 | 165 | 0.6992% | 300 | 465 | 389216 | 6339127 | 2.3095 | 2.1735 | 2.6374 | 4.5186 | 4518.56 | 409.47 | 0.18 | 26 | 33.23 | 73.6% | 71.28% | 4.9136 | 13.58% | 9:19 | 9:12 | Grid fail | 0:07 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:25 | 17:14 | 10:49 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of HT panel(iCR-2) have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 202 nos tables grass cutting were done by outside labour manually. 13. Today 49 nos tables grass cutting were done by grass cutting machine. 14. Today 88 nos tables grass cutting were done by TRACTOR machine.
2019-12-17 | 6:26 | 17:14 | 10:48 | 1425 | 3317 | 0 | 3478 | 3992 | 3877 | 7850 | 23939 | 23700 | 239 | 1.008% | 200 | 439 | 413155 | 6363066 | 2.3264 | 2.207 | 2.6141 | 4.3111 | 4311.14 | 400.55 | 0.34 | 26 | 32.61 | 75.91% | 73.69% | 4.8066 | 13.68% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:26 | 17:14 | 10:48 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of POWER TRANSFORMER(ICR-1) have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today 106 nos tables grass cutting were done by outside labour manually.
2019-12-18 | 6:28 | 17:17 | 10:49 | 1337 | 3140 | 0 | 3298 | 3880 | 3811 | 7460 | 22926 | 22800 | 126 | 0.5526% | 300 | 426 | 436081 | 6385992 | 2.228 | 2.1215 | 2.4842 | 4.2624 | 4262.44 | 384.97 | 0.26 | 26 | 33.03 | 75.52% | 73.19% | 4.6196 | 13.1% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:28 | 17:17 | 10:49 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of POWER TRANSFORMER(ICR-2) have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.
2019-12-19 | 6:29 | 17:17 | 10:48 | 1456 | 3495 | 0 | 3819 | 4371 | 4204 | 9053 | 26398 | 26200 | 198 | 0.7557% | 200 | 398 | 462479 | 6412390 | 2.5654 | 2.3793 | 3.0147 | 4.6468 | 4646.8 | 488.26 | 0.31 | 26 | 34.63 | 68.67% | 66.13% | 5.8591 | 15.09% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:29 | 17:17 | 10:48 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of HT SWITCHYARD have not been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today auditing was conducted by Mr. Suajn, Mr. Samaya & Investers (3 persons) only.
2019-12-20 | 6:29 | 17:17 | 10:48 | 651 | 1551 | 0 | 1764 | 2008 | 1926 | 3277 | 11177 | 11100 | 77 | 0.6937% | 200 | 277 | 473656 | 6423567 | 1.0862 | 1.0837 | 1.0912 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 6.388% | 13:50 | 10:00 | Grid failure due to substation matainanace | 3:50 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:29 | 17:17 | 10:48 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of HT SWITCHYARD have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today SCADA is not communicating so weather station value is not able to get.
2019-12-21 | 6:28 | 17:17 | 10:49 | 1227 | 2941 | 0 | 3212 | 3687 | 3495 | 7020 | 21582 | 21400 | 182 | 0.8505% | 300 | 482 | 495238 | 6445149 | 2.0974 | 1.9975 | 2.3377 | 3.8157 | 3815.67 | 346.42 | 0.24 | 25 | 30.68 | 79.01% | 77.28% | 4.157 | 12.34% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:28 | 17:17 | 10:49 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of Inverter Cleaning & Checking of ICR-1 have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today R.O. Plant cleaning have been completed. 13. Today street light checking form 121 to 149 have been completed.
2019-12-22 | 6:33 | 17:15 | 10:42 | 1609 | 3864 | 0 | 4129 | 4755 | 4484 | 9050 | 27891 | 27700 | 191 | 0.6895% | 200 | 391 | 523129 | 6473040 | 2.7105 | 2.5845 | 3.0137 | 5.1578 | 5157.75 | 479.09 | 0.26 | 26 | 34.1 | 74.63% | 72.03% | 5.7491 | 15.94% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:33 | 17:15 | 10:42 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of Inverter Cleaning & Checking of ICR-2 have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today Physical inspection of Lighting Arrester Checking have been completed.
2019-12-23 | 6:28 | 17:22 | 10:54 | 1268 | 2970 | 0 | 3180 | 3682 | 3593 | 7180 | 21873 | 21700 | 173 | 0.7972% | 300 | 473 | 545002 | 6494913 | 2.1257 | 2.0155 | 2.3909 | 4.0173 | 4017.31 | 359.19 | 0.22 | 25 | 31.34 | 76.64% | 74.77% | 4.3103 | 12.5% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:28 | 17:22 | 10:54 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. Physical inspection of fire alram & fire extingiusher have been completed. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Today Physical inspection of all SCADA Panels Checking have been completed. 13. Today Physical inspection of 33K.V. HT Panel (OG Panel) Checking have been completed.
2019-12-24 | 6:34 | 17:16 | 10:42 | 1182 | 2812 | 0 | 3047 | 3462 | 3272 | 6480 | 20255 | 20100 | 155 | 0.7711% | 200 | 355 | 565257 | 6515168 | 1.9684 | 1.8896 | 2.1578 | 3.568 | 3568.03 | 341.07 | 0.27 | 24 | 30.11 | 76.13% | 74.64% | 4.0928 | 11.58% | 8:45 | 8:35 | Grid Fail | 0:10 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:34 | 17:16 | 10:42 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Today Physical inspection of 33K.V. HT Panel (ICR-1 & ICR-2) Checking have been completed.
2019-12-25 | 6:29 | 17:22 | 10:53 | 1629 | 3896 | 0 | 4228 | 4803 | 4615 | 9400 | 28571 | 28400 | 171 | 0.6021% | 200 | 371 | 593828 | 6543739 | 2.7766 | 2.6298 | 3.1302 | 5.1765 | 5176.51 | 478 | 0.31 | 26 | 33.94 | 75.34% | 72.75% | 5.736 | 16.33% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:29 | 17:22 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Today Today 50 nos table grass side have been completed.
2019-12-26 | 6:32 | 17:25 | 10:53 | 836 | 2029 | 0 | 2215 | 2473 | 2365 | 4720 | 14638 | 14400 | 238 | 1.653% | 300 | 538 | 608466 | 6558377 | 1.4225 | 1.3605 | 1.5718 | 2.5054 | 2505.4 | 231.37 | 0.06 | 24.47 | 27.45 | 79.74% | 78.99% | 2.7764 | 8.366% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:32 | 17:25 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Today 60 nos table grass side have been completed.
2019-12-27 | 6:41 | 17:21 | 10:40 | 1205 | 2875 | 0 | 3113 | 3589 | 3475 | 6850 | 21107 | 21000 | 107 | 0.5095% | 200 | 307 | 629573 | 6579484 | 2.0512 | 1.9557 | 2.2811 | 3.8507 | 3850.74 | 351.96 | 0.24 | 26.39 | 31.85 | 77.12% | 75.09% | 4.2235 | 12.06% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:41 | 17:21 | 10:40 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Today 60 nos table grass side have been completed ICR-2. 12.Today monthly pending all street lights checking have been completed.
2019-12-28 | 6:40 | 17:22 | 10:42 | 1336 | 3159 | 0 | 3422 | 3858 | 3737 | 7460 | 22972 | 22800 | 172 | 0.7544% | 300 | 472 | 652545 | 6602456 | 2.2325 | 2.1278 | 2.4842 | 4.147 | 4146.98 | 380.02 | 1.2 | 23.57 | 29.78 | 77.5% | 76.07% | 4.5602 | 13.13% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:40 | 17:22 | 10:42 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Today 70 nos table grass side have been completed 3MW site.
2019-12-29 | 6:34 | 17:30 | 10:56 | 1622 | 3875 | 0 | 4183 | 4700 | 4561 | 9230 | 28171 | 28000 | 171 | 0.6107% | 200 | 371 | 680716 | 6630627 | 2.7377 | 2.5982 | 3.0736 | 5.0413 | 5041.33 | 458.21 | 0.36 | 23 | 31.1 | 77.14% | 75.33% | 5.4985 | 16.1% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:34 | 17:30 | 10:56 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less.
2019-12-30 | 6:20 | 17:10 | 10:50 | 1594 | 3800 | 0 | 4116 | 4678 | 4540 | 9150 | 27878 | 27600 | 278 | 1.007% | 200 | 478 | 708594 | 6658505 | 2.7092 | 2.569 | 3.047 | 5.0189 | 5018.86 | 461.17 | 0.77 | 22.27 | 29.86 | 76.54% | 75.12% | 5.534 | 15.93% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:20 | 17:10 | 10:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 12. Today Plot-1(3MW)20 nos table grass cutting completed with help of Machine.
2019-12-31 | 6:31 | 17:10 | 10:39 | 1539 | 3651 | 0 | 3979 | 4524 | 4330 | 8720 | 26743 | 26600 | 143 | 0.5376% | 300 | 443 | 735337 | 6685248 | 2.5989 | 2.4723 | 2.9038 | 4.3527 | 4352.73 | 524.3 | 0.57 | 23 | 32.15 | 65.7% | 63.89% | 6.2916 | 15.29% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB-7 3. INV-1.2, SMB-4 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. INV-1.1, SMB-5 | 6:31 | 17:10 | 10:39 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 12. Today (3MW )15 nos table grass cutting completed with help of Machine.

## Jan-20
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Jan-2020 | Cumulative (FY 2020-2021) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3003 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | m/s | (°C) | (°C) | (%) | (%) |  | (%)
2020-01-01 | 6:33 | 17:33 | 11:00 | 1182 | 2849 | 0 | 3129 | 3528 | 3458 | 6860 | 21006 | 20800 | 206 | 0.9904% | 200 | 406 | 21006 | 6706254 | 2.0414 | 1.9405 | 2.2844 | 3.7439 | 3743.93 | 383.63 | 0.78 | 23.23 | 29.02 | 68.28% | 67.23% | 4.6036 | 12.01% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:33 | 17:33 | 11:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 12. Today (3MW )18 nos table grass cutting completed with help of Machine. 13. Physical inspection of ICR-1, INV-1 all SMBs voltage and current cheking have been completed.
2020-01-02 | 6:46 | 17:26 | 10:40 | 423 | 967 | 0 | 1075 | 1203 | 1161 | 2260 | 7089 | 7000 | 89 | 1.271% | 200 | 289 | 28095 | 6713343 | 0.68892 | 0.66241 | 0.75258 | 1.105 | 1105.02 | 102.9 | 0.19 | 23.35 | 23.92 | 88.6% | 88.96% | 1.2348 | 4.052% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:46 | 17:25 | 10:39 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 12. Today Plot(3MW ) 2 -15 nos table grass cutting completed with help of Machine. 13. Physical inspection of ICR-1, INV-2 all SMBs voltage and current cheking have been completed.
2020-01-03 | 6:37 | 17:54 | 11:17 | 790 | 1809 | 0 | 2028 | 2241 | 2130 | 4240 | 13238 | 13100 | 138 | 1.053% | 200 | 338 | 41333 | 6726581 | 1.2865 | 1.2343 | 1.4119 | 2.2135 | 2213.51 | 206.52 | 1.021 | 25.101 | 27.587 | 77.93% | 77.15% | 2.4782 | 7.566% | 10:00:00 12:24 | 09:53:00 12:18 | Grid Failure | 00:07 00:06 Total 00:13 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:37 | 17:54 | 11:17 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. INV 1.1, SMB 5 has burnt. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 9. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 10. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 11. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 12. Today 35 Table Module down portion grass cutting at 3Mw (PLOT-3). 13. Physical inspection of ICR-1, INV-3 all SMBs voltage and current cheking have been completed.
2020-01-04 | 6:40 | 17:30 | 10:50 | 608 | 1394 | 0 | 1565 | 1751 | 1698 | 3270 | 10286 | 10100 | 186 | 1.842% | 200 | 386 | 51619 | 6736867 | 0.99961 | 0.96241 | 1.0889 | 1.6299 | 1629.92 | 150.97 | 0.28 | 23.09 | 24.9 | 86.27% | 86.3% | 1.8116 | 5.879% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:40 | 17:30 | 10:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3.. Due to rain All Modules Cleaned 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. INV 1.1, SMB 5 has burnt. 6. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 7. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down. 8. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 9. LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 10. INV 2.2 front display is showing wrong data(Energy AC Export). On Node 3 the value is showing less. 11. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 12. Again INV 2.2 display is showing wrong data(Energy AC Export). On Node 2, node 3 & node 4 are showing less. 13. Today ICR-1,24 nos Table Module grass cutting complet . 14. Physical inspection of ICR-2, INV-1 all SMBs voltage and current cheking have been not completed due to rain.
2020-01-05 | 6:38 | 17:28 | 10:50 | 1547 | 3460 | 0 | 3827 | 4061 | 4163 | 8320 | 25378 | 25200 | 178 | 0.7063% | 300 | 478 | 76997 | 6762245 | 2.4663 | 2.3399 | 2.7706 | 4.3683 | 4368.29 | 399.81 | 0.61 | 25.66 | 32.33 | 80.37% | 78.11% | 4.7977 | 14.51% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:38 | 17:28 | 10:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3.. Due to rain All Modules Cleaned 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 9. Physical inspection of ICR-2, INV-2 all SMBs voltage and current cheking have been completed.
2020-01-06 | 6:33 | 17:33 | 11:00 | 1733 | 3905 | 0 | 4289 | 4264 | 4663 | 9390 | 28244 | 28100 | 144 | 0.5125% | 200 | 344 | 105241 | 6790489 | 2.7448 | 2.5863 | 3.1269 | 5.0243 | 5024.3 | 448.51 | 0.96 | 24 | 32.12 | 78.53% | 76.38% | 5.3821 | 16.14% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 |  |  | 0:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3.. Due to rain All Modules Cleaned 4. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 5. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 7. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 8. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 9. Physical inspection of ICR-2, INV-3 all SMBs voltage and current cheking have been completed. 10. Today 61nos of Table grass cutting have been completed by 2 machine & 3 man power.
2020-01-07 | 6:35 | 17:32 | 10:57 | 1678 | 3738 | 0 | 4044 | 4071 | 4488 | 8970 | 26989 | 26700 | 289 | 1.082% | 300 | 589 | 132230 | 6817478 | 2.6228 | 2.4717 | 2.987 | 4.8107 | 4810.67 | 435.9 | 0.55 | 24.09 | 32 | 77.56% | 75.48% | 5.2308 | 15.43% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:35 | 17:35 | 11:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Pending Physical inspection of ICR-2, INV-1 all SMBs voltage and current cheking have been completed. 9. Today ICR-2, 61nos of Table grass cutting have been completed by 2 machine & 3 man power & ICR-1,16 nos of module cleaning have been completed. 10. Physical inspection of ICR-1, INV-1,2,3 cleaning & cheking have been completed.
2020-01-08 | 6:36 | 17:32 | 10:56 | 1763 | 3981 | 0 | 4316 | 4310 | 4641 | 9420 | 28431 | 28300 | 131 | 0.4629% | 200 | 331 | 160661 | 6845909 | 2.763 | 2.6078 | 3.1369 | 5.0913 | 5091.3 | 467.14 | 0.52 | 25 | 32.89 | 76.36% | 74.05% | 5.6057 | 16.25% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:36 | 17:32 | 10:56 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today ICR-2, 62nos of Table grass cutting have been completed by 2 machine & 3 man power & ICR-1,24 nos of module cleaning have been completed. 9. Physical inspection of ICR-2, INV-1,2,3 cleaning & cheking have been completed.
2020-01-09 | 6:39 | 17:30 | 10:51 | 1652 | 3775 | 0 | 3758 | 3739 | 4058 | 8810 | 25792 | 25500 | 292 | 1.145% | 300 | 592 | 186453 | 6871701 | 2.5065 | 2.3295 | 2.9337 | 4.795 | 4794.96 | 440.9 | 0.48 | 25.29 | 32.26 | 73.96% | 71.9% | 5.2908 | 14.74% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 7. ICR-2 | 1 to 6. 06:39 7-12:15 | 1 to 6. 17:30 7-12:30 | 1 to 6. 10:51 7. 15 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7.Emergency ICR-2 Transformer. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today ICR-2, 34 nos of Table grass cutting have been completed by 1 machine & 2 man power & ICR-1,19 nos of module cleaning have been completed. 9. Physical inspection of UPS &Battery charger(MCR,ICR-1&2) cleaning & cheking have been completed.
2020-01-10 | 6:37 | 17:29 | 10:52 | 1702 | 3870 | 0 | 4155 | 4649 | 4492 | 9030 | 27898 | 27700 | 198 | 0.7148% | 200 | 398 | 214351 | 6899599 | 2.7112 | 2.5882 | 3.007 | 4.8314 | 4831.43 | 448.77 | 0.88 | 26 | 33.67 | 78.47% | 75.86% | 5.3852 | 15.95% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:37 | 17:29 | 10:52 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today ICR-2, 30 nos of Table grass cutting have been completed by 1 machine & 2 man power & ICR-1,20 nos of module cleaning have been completed. 9. Physical inspection of all LT panels (MCR,ICR-1&2) cleaning & checking have been completed.
2020-01-11 | 6:50 | 17:31 | 10:41 | 1719 | 3941 | 0 | 4216 | 4757 | 4547 | 9010 | 28190 | 28000 | 190 | 0.6786% | 300 | 490 | 242541 | 6927789 | 2.7396 | 2.631 | 3.0003 | 4.9509 | 4950.91 | 463.84 | 0.83 | 26 | 33.72 | 78.04% | 75.42% | 5.5661 | 16.11% | 6:48 | 6:40 | Grid Failure | 0:08 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:50 | 17:31 | 10:41 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today grass dumping done by 3 persons. 9. Physical inspection of all RTU & MTU Panel cleaning & checking have been completed.
2020-01-12 | 6:35 | 17:30 | 10:55 | 2083 | 4719 | 0 | 5080 | 5765 | 5456 | 11040 | 34143 | 33900 | 243 | 0.7168% | 200 | 443 | 276684 | 6961932 | 3.3181 | 3.1691 | 3.6763 | 6.038 | 6038.04 | 547.23 | 0.92 | 25 | 34.27 | 78.4% | 75.61% | 6.5668 | 19.51% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:35 | 17:30 | 10:55 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Rspective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today grass dumping done by 3 persons. 9. Physical inspection of WMS cleaning & checking have been completed.
2020-01-13 | 6:34 | 17:31 | 10:57 | 2048 | 4637 | 0 | 5005 | 5666 | 5400 | 11080 | 33836 | 33600 | 236 | 0.7024% | 300 | 536 | 310520 | 6995768 | 3.2882 | 3.1215 | 3.6896 | 6.002 | 6002.01 | 543.91 | 0.62 | 24.45 | 34.2 | 77.93% | 75.18% | 6.5269 | 19.34% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:34 | 17:31 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today grass dumping done by 5 persons 7 trip with the help of tractor. 9. Physical inspection of Fire Alarm cleaning & checking have been completed,ICR-1 fire alarm not working. 10.Today ICR-2, 36 nos of Table grass cutting have been completed by 1 machine & 2 man power ICR-1,20 nos of module cleaning have been completed.
2020-01-14 | 6:36 | 17:33 | 10:57 | 1950 | 4442 | 0 | 4777 | 5402 | 5140 | 10520 | 32231 | 32000 | 231 | 0.7219% | 100 | 331 | 342751 | 7027999 | 3.1323 | 2.9782 | 3.5032 | 5.7336 | 5733.6 | 521.8 | 0.26 | 25 | 33.91 | 77.38% | 74.73% | 6.2616 | 18.42% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:36 | 17:33 | 10:57 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Today grass dumping done by 5 persons 7 trip with the help of tractor. 9. Physical inspection of HT Panel(MCR Outgoing) cleaning & checking have not been completed due to other work. 10.Today 3mw, 18 nos of Table grass cutting have been completed by 1 machine in first shift, R.O. plant side road grass cleaning at 2nd shift. 2 man power ICR-1,10 nos of module cleaning have been completed at 1st shift in 2nd shift bush cutting done mannually.
2020-01-15 | 6:40 | 17:33 | 10:53 | 1707 | 3923 | 0 | 4135 | 4717 | 4469 | 9070 | 28021 | 27900 | 121 | 0.4337% | 300 | 421 | 370772 | 7056020 | 2.7231 | 2.5996 | 3.0203 | 4.9489 | 4948.93 | 448.74 | 0.34 | 25 | 32.73 | 78.7% | 76.37% | 5.3849 | 16.02% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:40 | 17:33 | 10:53 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of HT Panel(ICR-1) cleaning & checking have not been completed due to other work. 9.Today ICR-1, 20 nos of Table grass cutting have been completed by 1 machine in first shift & R.O. plant pipe repairing.
2020-01-16 | 6:40 | 17:34 | 10:54 | 1734 | 3962 | 0 | 4233 | 4767 | 4532 | 9190 | 28418 | 28200 | 218 | 0.773% | 200 | 418 | 399190 | 7084438 | 2.7617 | 2.6376 | 3.0603 | 5.6164 | 5616.42 | 513.79 | 0.45 | 24 | 33.48 | 69.61% | 67.34% | 6.1655 | 16.24% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:40 | 17:34 | 10:54 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of HT Panel(ICR-2) cleaning & checking have not been completed due to other work. 9. Today street light checking has been checking completed.
2020-01-17 | 6:35 | 17:09 | 10:34 | 1836 | 4196 | 0 | 4518 | 5034 | 4808 | 9700 | 30092 | 29800 | 292 | 0.9799% | 300 | 592 | 429282 | 7114530 | 2.9244 | 2.7973 | 3.2301 | 5.3365 | 5336.45 | 505.65 | 0.83 | 25 | 34.46 | 77.26% | 74.45% | 6.0678 | 17.2% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:35 | 17:09 | 10:34 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of Power Transformer(ICR-1) cleaning & checking have not been completed due to other work. 9. Today street light 23 to 55 checking has been checking completed.
2020-01-18 | 6:36 | 17:51 | 11:15 | 1744 | 3939 | 0 | 4129 | 4711 | 4577 | 9270 | 28370 | 28100 | 270 | 0.9609% | 200 | 470 | 457652 | 7142900 | 2.757 | 2.62 | 3.0869 | 5.1122 | 5112.21 | 467.02 | 0.93 | 27 | 34.94 | 74.07% | 71.24% | 5.6042 | 16.22% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.1, SMB- 7 3. INV-1.1, SMB-6 & 5 4. INV-1.2, SMB-5 5. LT Panel -2, ACCB - 7 6. LT Panel -1, ACCB - 1 | 6:36 | 17:51 | 11:15 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of Power Transformer(ICR-2) cleaning & checking have been completed . 9. Today street light 56 to 66 checking has been checking completed. 10.Today ICR-1 , 5 nos of Street Lights changing have been completed.
2020-01-19 | 6:36 | 17:39 | 11:03 | 1654 | 3924 | 0 | 4101 | 4735 | 4509 | 9150 | 28073 | 27900 | 173 | 0.6201% | 300 | 473 | 485725 | 7170973 | 2.7282 | 2.5957 | 3.047 | 5.0235 | 5023.53 | 452 | 0.64 | 26 | 34.42 | 77.1% | 74.31% | 5.424 | 16.05% |  |  |  | 0 | 1. ICR-1, INV-3 2. INV-1.2, SMB-5 3. LT Panel -2, ACCB - 7 4. LT Panel -1, ACCB - 1 5. 2. INV-1.1, SMB- 7 6. INV-1.1, SMB-6 & 5 7. INV 1.1 | 1 TO 6 : 06:36:00 7 : 15:05 | 1 TO 4 : 17:39:00 5 & 6 : 15 :04 7 : 17:39 | 1 TO 4 : 11:03 5 & 6 : 8:28 7 : 2:34 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. SMB burn. 5. MCCBs have burnt. 6. Cable(LT panel to ACCB) have fault. 7. Emergency Shutdown for SMBs replacement from INV 1.3 to INV 1.1 | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of Power Transformer(ICR-2) cleaning & checking have been completed . 9. Today street light 67 to 88 checking have not been checking completed due to other work. 10.Today We have repalced two SMBs from INV 1.3(which was down) to INV 1.1 SMB #5 & #6. Tommorrow we will replace remaining one SMB(INV 2.1 SMB #5).
2020-01-20 | 6:36 | 17:39 | 11:03 | 1631 | 3489 | 0 | 4100 | 4558 | 4344 | 8780 | 26902 | 26600 | 302 | 1.135% | 300 | 602 | 512627 | 7197875 | 2.6144 | 2.4859 | 2.9237 | 4.8367 | 4836.74 | 429.82 | 0.49 | 26 | 33.92 | 77.7% | 75.04% | 5.1578 | 15.38% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -2, ACCB - 7 3. LT Panel -1, ACCB - 1 4. INV-1.1, SMB- 7 5. INV-1.1, SMB-6 & 5 6. INV-1.2, SMB-5 7. INV-1.2, SMB-5 8. INV 1.2 | 1 to 5 : 06:36:00 6 : 06:36 7: 9:25 8 : 6:55 | 1 to 5 : 17:39:00 6: 6:54 7: 14:30 8 : 9:25 | 1 to 5 : 11:03 6: 00:18 7: 05:05 8 : 2:30 | 1. AC cable side blast and LV cable issue. 2. MCCBs have burnt. 3. Cable(LT panel to ACCB) have fault. 4. SMB burn. 5. Due to communication card burn.(Replacement is on process) 6. SMB burn. 7. After replacement time taken for string check. 8. Emergency Shutdown for SMBs replacement from INV 1.3 to INV 1.2 | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection of Ht Switchyard cleaning & checking have been completed . 9. Today street light 89 to 120 checking have not been checking completed due to other work. 10.Today We have repalced one SMB(INV 2.1 SMB #5).
2020-01-21 | 6:38 | 17:27 | 10:49 | 1886 | 3792 | 0 | 3602 | 4104 | 3972 | 7980 | 25336 | 25200 | 136 | 0.5397% | 200 | 336 | 537963 | 7223211 | 2.4622 | 2.3808 | 2.6573 | 4.3183 | 4318.33 | 395.2 | 0.78 | 27 | 33.72 | 81.3% | 78.58% | 4.7424 | 14.48% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -2, ACCB - 7 3. LT Panel -1, ACCB - 1 4. INV-1.1, SMB- 7 5. INV 1.1, SMB 5 6. INV 1.1, SMB-6 | 6:38 | 1 to 4. 17:27 5. 13:36 6. 13:39 | 1 to 4. 10:49 5. 6:58 6. 7:01 | 1. AC cable side blast and LV cable issue. 2. MCCBs have burnt. 3. Cable(LT panel to ACCB) have fault. 4. SMB burn. 5. Before SMB staring with String Checking 6. Before SMB staring with String Checking | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB-6&7 and INV-1.2 at SMB 5 com-card was burn, INV-1.1, SMB-6&5 communication was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection & cleaning of all inverters of ICR-1 have been completed . 9. Today street light 89 to 147 checking have been checking completed. Also we have changed 3 street light. 10.Today We have repalced two batteries of firealarm of ICR-2. 11. Today we have 4nos of Strings rectification work at INV 1.1 & INV 1.2 SMBs. 12. Physical inspection & cleaning of HT Panel of ICR-1 & MCR Outgoing have been completed .
2020-01-22 | 6:36 | 17:48 | 11:12 | 3094 | 4650 | 0 | 4183 | 4848 | 4632 | 9370 | 30777 | 30500 | 277 | 0.9082% | 300 | 577 | 568740 | 7253988 | 2.991 | 2.9365 | 3.1202 | 5.1067 | 5106.66 | 460.6 | 0.67 | 27 | 35.27 | 81.84% | 78.61% | 5.5272 | 17.59% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -2, ACCB - 7 3. LT Panel -1, ACCB - 1 4. INV-1.1, SMB- 7 | 6:36 | 17:48 | 11:12 | 1. AC cable side blast and LV cable issue. 2. MCCBs have burnt. 3. Cable(LT panel to ACCB) have fault. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA. 8. Physical inspection & cleaning of all inverters of ICR-2 have been completed . 9. Today 40 metres street light cable(4C X 16 sq mm) changing & Also we have changed 3 street light. 10.Depending upon today schedule LA checking have been completed. 11.Today ICR-2, 40nos of Table grass cutting have been completed by 2 machine & 3 man power & 2nd shift ICR-2 down site road grass cutting have been completed.
2020-01-23 | 6:45 | 17:40 | 10:55 | 2982 | 4457 | 0 | 4122 | 4716 | 4463 | 9010 | 29750 | 29500 | 250 | 0.8475% | 200 | 450 | 598490 | 7283738 | 2.8912 | 2.845 | 3.0003 | 4.9891 | 4989.11 | 442.34 | 0.4 | 27.1 | 34.82 | 84.51% | 81.32% | 5.3081 | 17% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -2, ACCB - 7 3. LT Panel -1, ACCB - 1 4. INV-1.1, SMB- 7 | 6:45 | 17:40 | 10:55 | 1. AC cable side blast and LV cable issue. 2. MCCBs have burnt. 3. Cable(LT panel to ACCB) have fault. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.. 8.Today pending schedule HT & ICOG-1 cleaning & checking have been completed. 9.Today ICR-1, 40nos of Table grass cutting have been completed by 2 machine & 3 man power & 2nd shift Hill site road grass cutting have been completed.
2020-01-24 | 6:34 | 17:50 | 11:16 | 3101 | 4567 | 0 | 4250 | 4798 | 4633 | 9300 | 30649 | 30400 | 249 | 0.8191% | 200 | 449 | 629139 | 7314387 | 2.9785 | 2.9285 | 3.0969 | 5.169 | 5169.04 | 458.3 | 0.65 | 27.9 | 36.05 | 81.42% | 77.97% | 5.4996 | 17.52% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -2, ACCB - 7 3. LT Panel -1, ACCB - 1 4. INV-1.1, SMB- 7 | 6:34 | 17:50 | 11:16 | 1. AC cable side blast and LV cable issue. 2. MCCBs have burnt. 3. Cable(LT panel to ACCB) have fault. 4. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. MCCB of INV 28, 29, 30 & 32 (3Mw plant) are burn at ACCB-7. Respective Inveters are also down & LT PANEL-1, ACCB-1 feeder was trip due to cable fault. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3, INV #30 of 3mw new site are not communicating with SCADA.. 8.Today pending schedule ICR-1 power transformer & Auxallary transforme cleaning & checking not have been completed due to other work 9.RO plant(7M)w pipeline broken replacement not have been complted. 10.Today we are change In ACCB-7(3MW) 2nos MCCB,tomorrow doing another 2nos. 11. Auxiliary Teansformer has reached at site and unloading have completed. 12.Today fencing cutting at konda site has been done.
2020-01-25 | 6:37 | 17:18 | 10:41 | 2759 | 4131 | 0 | 3840 | 4318 | 4063 | 8760 | 27871 | 27600 | 271 | 0.9819% | 200 | 471 | 657010 | 7342258 | 2.7086 | 2.6215 | 2.9171 | 4.6226 | 4622.59 | 419.31 | 0.78 | 26 | 33.75 | 85.35% | 82.48% | 5.0317 | 15.93% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 4. LT Panel -2, ACCB - 7 | 6:37 | 1. to 3. 17:18 4. 12:24 | 1. to 3. 10:41 4. 05:47 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. 4. Shutdown for MCCB replacement work | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9.Today we have changed MCCBs In ACCB-7(3MW) & also cable termination complete at Inverter end. 10.Today fencing cutting at konda site is going on. 11. Today String checking have completed on replaced SMBs (1.1.5, 1.1.6 & 1.2.5)
2020-01-26 | 6:37 | 17:44 | 11:07 | 3146 | 4539 | 0 | 4133 | 4760 | 4501 | 10260 | 31339 | 31200 | 139 | 0.4455% | 400 | 539 | 688349 | 7373597 | 3.0456 | 2.8915 | 3.4166 | 5.0479 | 5047.85 | 449.85 | 0.35 | 27 | 35.32 | 85.96% | 82.56% | 5.3982 | 17.91% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 | 6:37 | 17:44 | 11:07 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9.Today fencing cutting at konda site is going on. 10. Today We clean Pantry and Store & categorised the material according the application.
2020-01-27 | 6:43 | 17:33 | 10:50 | 3422 | 4875 | 0 | 4604 | 5189 | 4993 | 11350 | 34433 | 34200 | 233 | 0.6813% | 200 | 433 | 722782 | 7408030 | 3.3463 | 3.1664 | 3.7796 | 5.7019 | 5701.87 | 526.56 | 0.93 | 28 | 36.63 | 82.8% | 79.1% | 6.3187 | 19.68% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 | 6:43 | 17:33 | 10:50 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9.Today fencing cutting at konda site is going on. In second half we have done cable dressing of modules. 10. 240 mm² cable drum have reached at site.
2020-01-28 | 6:47 | 17:47 | 11:00 | 1500 | 3676 | 0 | 3390 | 3799 | 3620 | 8120 | 24105 | 23900 | 205 | 0.8577% | 200 | 405 | 746887 | 7432135 | 2.3426 | 2.1927 | 2.704 | 4.0424 | 4042.37 | 356.22 | 0.96 | 27 | 31.99 | 84.39% | 82.12% | 4.2746 | 13.78% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 4. INV 1.1 | 1. to. 3. 06:47:00 4. 8:48 | 1. to 3. 17:47:00 4. 9:50 | 1. to3. 11:00 4. 01:02 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. 4. DC Ground Fault | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9.Today 24 table grass cutting were done by one manpower. Two man power have done cable dressing( ICR-1 completed, ICR-2 40% pending) 10. Y-Connector to SMB input cable laying was done for 1.1.4.8 string.
2020-01-29 | 6:35 | 18:01 | 11:26 | 2974 | 4839 | 0 | 4492 | 5067 | 4848 | 10950 | 33170 | 32900 | 270 | 0.8207% | 300 | 570 | 780057 | 7465305 | 3.2235 | 3.048 | 3.6464 | 5.469 | 5468.96 | 480.13 | 1.24 | 27 | 33.53 | 82.89% | 80.17% | 5.7616 | 18.96% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 | 6:35 | 18:01 | 11:26 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9.Today total plant done cable dressing have ben completed. 10. today 3Mw street lights & all Gate numbering have been completed.
2020-01-30 | 6:54 | 17:23 | 10:29 | 1309 | 2279 | 0 | 3235 | 3562 | 3373 | 7600 | 21358 | 21100 | 258 | 1.223% | 300 | 558 | 801415 | 7486663 | 2.0756 | 1.8872 | 2.5308 | 3.2068 | 3206.76 | 356.24 | 0.42 | 26 | 32.24 | 78.45% | 76.27% | 4.2749 | 12.21% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 4. INV 1.1 5. INV 1.1 & INV 1.2 6. INV 1.1 & INV 1.2 | 1. to 3. 6:54 4. INV 1.1 & INV 1.2 : 12:45 5. INV 1.1 & INV 1.2: 13:01 6. INV 1.1 & INV 1.2: 17:01 | 1. to 3. 17:23 4. INV 1.1 & INV 1.2 : 13:05 5. INV 1.1 & INV 1.2 : 15:28 6. INV 1.1 & INV 1.2: 17:23 | 1. to 3. 10:29 4. INV 1.1 & INV 1.2. 00:20 5. INV 1.1 & INV 1.2 : 02:27 6. INV 1.1 & INV 1.2: 00:22 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. 4. Emergency shutdown for INV 1.3 testing 5. INV AUXILARY SUPPLY FAILURE 6. Incommer shutdown for neutral wire replacement | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9. Today camera cable execution was going on. 10. Service Engineer (Mr. Anil) have reached at site for checking of INV 1.3
2020-01-31 | 6:35 | 17:32 | 10:57 | 2133 | 3353 | 0 | 3711 | 4110 | 3950 | 8790 | 26047 | 25800 | 247 | 0.9574% | 200 | 447 | 827462 | 7512710 | 2.5313 | 2.3672 | 2.9271 | 4.5371 | 4537.09 | 402.41 | 1.29 | 27 | 33.22 | 81.09% | 78.53% | 4.8289 | 14.89% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 4. INV 1.1 & INV 1.2 | 1. TO 3. : 06:35 4. 11:18 | 1. TO 3. : 17:32 4. 11:55 | 1. TO 3. : 10:57 4. 00:37 | 1. AC cable side blast and LV cable issue. 2. Cable(LT panel to ACCB) have fault. 3. SMB burn. 4. Emergency shutdown for INV 1.3 testing | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9. Today camera cable execution was going on. 10. Service Engineer (Mr. Anil) have reached at site for checking of INV 1.3 11. IT Rack fixing was pending.

## Feb-20
VEH - Vizianagaram, 7.29 MW & 3 MW
O & M By: Inspire Clean Energy Pvt. Ltd.
Daily Generation Report
| Generation Hours |  |  | Inverters Reading | [6 empty] | Power Generation | [20 empty] | Grid OFF Details |  |  |  | Breakdown Details
Date | Generation Hours |  |  | Day Wise Inverters Reading | [6 empty] | Day's Generation (all inverters) | Day's Generation (Meters) | Difference | % loss | Import | Total Plant Consumption | Cumulative Feb-2020 | Cumulative (FY 2020-2021) | Specific Yield (kWh/kWp) | Specific Yield (kWh/kWp) 7290 kWp | Specific Yield (kWh/kWp) 3003 kWp | Total irradiation (KWh/sq.m) | Total irradiation(Wh/sq.m) | Average Irradiation (W/m^2) | Avg. Wind Speed | Avg. Ambient Temp. | Avg. Module Temp. | Performace Ratio | Weathered PR (%) | Pyranometer Value | P.L.F or C.U.F | Grid Start Time | Grid Stop Time | Reason of Grid failure & action | Total Plant Down Time | Effected ITC or ICR no. | Start Time | Stop Time | Total Plant Down Time | Reason of Breakdown & action | Daily Activities Summary
| Start Time | Stop Time | Total Time | INV 1.1 | INV 1.2 | INV 1.3 | INV 2.1 | INV 2.2 | INV 2.3 | New 3MWP | kWh | kWh | kWh | % | kWh | kWh | kWh | kWh | kWh/kWp | (kWh/kWp) | (kWh/kWp) | KWh/sq.m | Wh/sq.m | W/m2 | m/s | (°C) | (°C) | (%) | (%) |  | (%)
2020-02-01 | 6:42 | 17:32 | 10:50 | 1477 | 2434 | 0 | 2293 | 2533 | 2411 | 5370 | 16518 | 16400 | 118 | 0.7195% | 200 | 318 | 16518 | 7529228 | 1.6052 | 1.5292 | 1.7882 | 2.7165 | 2716.54 | 236.85 | 1.55 | 25 | 28.47 | 88.31% | 87.13% | 2.8422 | 9.441% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 | 6:42 | 17:32 | 10:50 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9. Today we have cleaned MCR & MCR surroundings. 10. 31nos of table grass cutting have been completed by one man power.
2020-02-02 | 6:35 | 17:42 | 11:07 | 1595 | 2606 | 0 | 2542 | 2772 | 2572 | 5900 | 17987 | 17800 | 187 | 1.051% | 300 | 487 | 34505 | 7547215 | 1.748 | 1.658 | 1.9647 | 2.8992 | 2899.17 | 237.22 | 0.82 | 25 | 28.27 | 93.56% | 92.39% | 2.8466 | 10.28% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1 3. INV-1.1, SMB- 7 4. LT Panel - 1 | 1. to 3. 06:35:00 4. 16:00 | 1. to 3. 17:42:00 4. 17:00 | 1. to 3. 11:00 4. 01:00 | 1. AC cable side blast and LV cable issue. 2. SMB burn. 3. Due to communication card burn. 4. Emergency Shutdown for ACCB-1 exeution. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 6. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 7. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 8. RO plant(7M)w pipeline broken replacement not have been completed. 9. Physical inspection of ICR-1, INV-2 SMB-7 voltage and current checking have been completed,due to cloudy weather other SMBs not checking have been completed.
2020-02-03 | 6:35 | 17:45 | 11:10 | 2125 | 3545 | 0 | 3534 | 3769 | 3578 | 7900 | 24451 | 24200 | 251 | 1.037% | 300 | 551 | 58956 | 7571666 | 2.3762 | 2.2704 | 2.6307 | 3.9914 | 3991.38 | 353.28 | 1.72 | 26.27 | 31.85 | 85.02% | 82.78% | 4.2394 | 13.98% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 4.LT Panel-1,ACCB-1 | 1 to 3-06:35:00 4.06:35 | 1 to 3 17:45:00 4. 14:15 | 1 to 3. 11:10 4. 07:40 | 1. AC cable side blast and LV cable issue. 2.String INV-3 problem. 3. Due to communication card burn. 4. Cable(LT panel to ACCB) have fault. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. INV #1, INV #2, INV #3 of 3mw new site are not communicating with SCADA. 7. RO plant(7M)w pipeline broken replacement not have been completed. 8. Physical inspection of ICR-1, INV-3 all SMBs voltage checking have been completed,due to INV down current not checking have been completed. 9.Today LT panel -1(3Mw) ACCB-1 running without string INV-3 .
2020-02-04 | 9:06 | 17:01 | 7:55 | 1049 | 1715 | 0 | 1669 | 1824 | 1751 | 3470 | 11478 | 11400 | 78 | 0.6842% | 0 | 78 | 70434 | 7583144 | 1.1155 | 1.0985 | 1.1555 | 1.7867 | 1786.67 | 225.35 | 0.93 | 25 | 28.61 | 88.25% | 87.03% | 2.7042 | 6.56% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 | 9:06 | 17:01 | 7:55 | 1. AC cable side blast and LV cable issue. 2.String INV-3 internal problem. 3. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. RO plant(7M)w pipeline broken replacement not have been completed. 7. Physical inspection of ICR-2, INV-1 all SMBs voltage checking have not been completed,due to cloudy weather.
2020-02-05 | 6:55 | 17:50 | 10:55 | 2381 | 3846 | 0 | 3498 | 3898 | 3832 | 7800 | 25255 | 25200 | 55 | 0.2183% | 0 | 55 | 95689 | 7608399 | 2.4543 | 2.3944 | 2.5974 | 4.2295 | 4229.5 | 380.99 | 0.98 | 27 | 32.79 | 83.29% | 80.8% | 4.5719 | 14.43% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 | 6:55 | 17:50 | 10:55 | 1. AC cable side blast and LV cable issue. 2.String INV-3 internal problem. 3. Due to communication card burn. | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. RO plant(7M)w pipeline broken replacement have been completed. 7. Physical inspection of ICR-2, INV-2 all SMBs voltage checking have been completed.
2020-02-06 | 6:36 | 17:49 | 11:13 | 2276 | 3692 | 0 | 3480 | 3913 | 3737 | 7900 | 24998 | 24700 | 298 | 1.206% | 200 | 498 | 120687 | 7633397 | 2.4293 | 2.3454 | 2.6307 | 4.0549 | 4054.86 | 3587.53 | 1.68 | 26 | 32.06 | 8.522% | 8.291% | 43.0504 | 14.29% |  |  |  | 0 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 4. Node-1 of INV-2.1 | 6:36 | 17:49 | 11:13 | 1. AC cable side blast and LV cable issue. 2.String INV-3 internal problem. 3. Due to communication card burn. 4. AC Magnectic Protetion | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. RO plant(7M)w pipeline broken replacement have been completed. 7. Physical inspection of ICR-2, INV-3 all SMBs voltage checking have been completed.
2020-02-07 | 6:34 | 17:51 | 11:17 | 1853 | 2980 | 0 | 2736 | 3067 | 2988 | 7280 | 20904 | 20800 | 104 | 0.5% | 300 | 404 | 141591 | 7654301 | 2.0315 | 1.8689 | 2.4242 | 4.508 | 4508.03 | 406.74 | 1.75 | 26.99 | 32.26 | 62.48% | 60.74% | 4.8809 | 11.95% | 1. 11:29 2. 11:55 3. 13:12 | 1. 11:24 2. 11:41 3. 11:55 | 1. Over voltage 2.Grid fail 3. Grid Fail | 1. 00:05:00 2. 00:14:00 3. 01:17:00 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 4. Node-1 of INV-2.1 | 6:34 | 17:51 | 11:17 | 1. AC cable side blast and LV cable issue. 2.String INV-3 internal problem. 3. Due to communication card burn. 4. AC Magnectic Protetion | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. RO plant(7M)w pipeline broken replacementnot completed. 7. Physical inspection of ICR-1, INV-1,2,3 cleaning & cheking have been completed. 8.Today ICR-1, 16 table grass have been completed. 9..LT panel -1(3Mw) ,ACCB-1 running without string INV-3.
2020-02-08 | 6:39 | 17:35 | 10:56 | 1592 | 2241 | 0 | 2504 | 2746 | 2623 | 6360 | 18066 | 17800 | 266 | 1.494% | 200 | 466 | 159657 | 7672367 | 1.7557 | 1.6058 | 2.1179 | 2.7711 | 2771.11 | 251.69 | 1 | 26 | 29.64 | 90.06% | 88.45% | 3.0203 | 10.33% |  |  |  | 0:00 | 1. ICR-1, INV-3 2. LT Panel -1, ACCB - 1,INV-3 3. INV-1.1, SMB- 7 4. INV 1.2 5. Node-4 of INV-1.2 | 1. to 4. 06:39 5. 10:03 | 1. to 3. 17:35 4. 17:35 | 1. to 3. 10:56 4. 03:23 5. 07:32 | 1. AC cable side blast and LV cable issue. 2.String INV-3 internal problem. 3. Due to communication card burn. 4. DC Breaker Issue 5. Communicaton Issue on Node 4 | 1. Daily Visual inspection. 2. Inspection Done by SCADA. 3. INV-1.3 at SMB- 2 to 7 communication card was burn and INV-1.1, SMB-7 full burn due to rain and ground fault. 4. ICR-1,INV-1 & 2 running but aux transformer is isolated condition and Auxiliary supply given from MCR. 5. Two nos of battery have some issue in ICR - 2 UPS. UPS isn't supporting battery bank. Now it is running without backup (Bypass Mode). 6. Due to heavy rain all modules clean. 7. Physical inspection of ICR-2, INV-1,2,3 cleaning & cheking have been completed. 8.Today R.O. Plant lekage repair work have going on. Finally we need a plumber who will make thread on HDPE pipe and do the rest work. 9..LT panel -1(3Mw) ,ACCB-1 running without string INV-3.
2020-02-09 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-10 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-11 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-12 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-13 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-14 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-15 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-16 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-17 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-18 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-19 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-20 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-21 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-22 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-23 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-24 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-25 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-26 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-27 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-28 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00
2020-02-29 |  |  | 0:00 | [7 empty] | 0 |  | 0 | #DIV/0! |  | 0 | 159657 | 7672367 | 0 | 0 | 0 | 0 | [5 empty] | #DIV/0! | #DIV/0! | 0 | 0% |  |  |  | 0 |  |  |  | 0:00